## Hourly Avg Data
Date | >0 | Load | COAL RATE | BLR RHS PRIMARY SH SPRAY | BLR RHS SECONDARY SH SPRAY | BLR LHS PRIMARY SH SPRAY | BLR LHS SECONDARY SH SPRAY | RHS RH DESPRHT TOTAL FLOW | LHS RH DESPRHT TOTAL FLOW | TOTAL AIR FLOW | APH-A I/L GAS O2% | APH-B I/L GAS O2% | APH-B O/L FG TEMP-1 | APH-B O/L FG TEMP-2 | APH-B O/L FG TEMP-3 | APH-A O/L FG TEMP-1 | APH-A O/L FG TEMP-2 | APH-A O/L FG TEMP-3 | APH-B FG DP | APH-A FG DP | TOTAL SECONDARY AIR FLOW | TOTAL PRIMARY AIR FLOW | OPACITY
Dozing started
2024-12-12 | 45638.5 | 576.0839 | 0.62842 | 127.6962 | 22.3341 | 111.7731 | 25.2298 | 47.3425 | 33.6136 | 1988.6949 | 3.743 | 3.3971 | 135.5807 | 130.0534 | 114.8206 | 144.9727 | 156.9335 | 154.3873 | 1131.9926 | 1374.9553 | 1136.6533 | 852.0434 | 21.7399
2024-12-12 | 45638.5417 | 464.2277 | 0.61741 | 95.6615 | 9.6971 | 84.4593 | 15.0773 | 40.3321 | 10.9605 | 1724.9111 | 4.5609 | 3.8782 | 130.7161 | 126.6163 | 112.2463 | 140.29 | 151.4533 | 149.5966 | 889.2634 | 1085.7163 | 1003.8747 | 721.0806 | 20.1069
2024-12-12 | 45638.5833 | 356.2931 | 0.67225 | 83.2185 | 4.7057 | 72.1222 | 7.751 | 36.5233 | 2.3192 | 1510.8301 | 5.0018 | 4.1496 | 122.4248 | 119.2493 | 106.6658 | 127.1308 | 137.4724 | 135.4523 | 683.3773 | 792.3889 | 851.0966 | 659.6879 | 3.5416
2024-12-12 | 45638.625 | 462.16 | 0.6706 | 107.1465 | 13.3699 | 99.6207 | 29.9398 | 45.2809 | 12.6629 | 1723.2366 | 3.7727 | 3.408 | 131.2112 | 126.7536 | 113.2004 | 132.6855 | 143.35 | 141.4976 | 881.4946 | 989.6258 | 916.1447 | 807.0724 | 1.1946
2024-12-12 | 45638.6667 | 581.2974 | 0.63756 | 135.8821 | 19.7396 | 117.3902 | 23.9773 | 52.2682 | 37.0929 | 2028.3616 | 3.1756 | 3.3934 | 138.2915 | 132.7278 | 117.702 | 143.3064 | 155.1956 | 152.4896 | 1174.1791 | 1375.2622 | 1171.2882 | 857.0945 | 9.6044
2024-12-12 | 45638.7083 | 586.8439 | 0.63906 | 130.2723 | 22.649 | 111.5991 | 17.8605 | 51.8251 | 39.6479 | 2037.6392 | 2.9198 | 3.5927 | 136.2508 | 130.5194 | 115.5942 | 146.4854 | 158.6109 | 155.7732 | 1152.9794 | 1421.5189 | 1198.8331 | 838.8318 | 16.4322
2024-12-12 | 45638.75 | 593.2083 | 0.62925 | 130.4161 | 23.1318 | 108.0883 | 25.8925 | 52.2227 | 37.0648 | 2021.2651 | 3.3338 | 3.4143 | 135.3691 | 129.5353 | 114.5697 | 145.8054 | 158.1874 | 155.0934 | 1133.3474 | 1403.8453 | 1185.316 | 835.9801 | 18.7565
2024-12-12 | 45638.7917 | 595.5359 | 0.62337 | 113.3961 | 19.8971 | 98.1231 | 22.7009 | 47.9043 | 37.909 | 2013.9641 | 3.2747 | 3.3081 | 135.46 | 129.5951 | 114.4885 | 145.0741 | 157.4209 | 154.4923 | 1137.7224 | 1391.5555 | 1174.2632 | 839.6908 | 14.5171
2024-12-12 | 45638.8333 | 589.4706 | 0.62943 | 110.8745 | 19.7209 | 92.5297 | 23.8942 | 47.3103 | 41.2645 | 1997.1782 | 3.0893 | 3.2127 | 135.8179 | 130.3426 | 114.8747 | 145.056 | 155.7439 | 153.8086 | 1139.2415 | 1379.9285 | 1159.2677 | 837.9371 | 8.7222
2024-12-12 | 45638.875 | 586.4309 | 0.62116 | 98.5703 | 20.7793 | 95.1599 | 24.1118 | 46.8997 | 39.4931 | 1991.212 | 3.3359 | 3.2892 | 134.6487 | 128.8913 | 113.633 | 143.1664 | 155.5307 | 152.4884 | 1126.74 | 1364.3728 | 1150.9257 | 840.2487 | 13.6982
2024-12-12 | 45638.9167 | 539.4585 | 0.61458 | 91.9374 | 14.5916 | 83.8997 | 17.7834 | 41.9508 | 37.4854 | 1847.9957 | 3.4941 | 3.4451 | 131.138 | 125.9781 | 111.1614 | 140.1069 | 152.3219 | 149.1018 | 997.9697 | 1211.559 | 1098.2618 | 749.7037 | 13.0663
2024-12-12 | 45638.9583 | 429.2371 | 0.60165 | 87.3737 | 6.8593 | 69.673 | 14.1589 | 25.334 | 6.8921 | 1566.4156 | 3.9546 | 4.0089 | 125.0888 | 121.1637 | 107.6811 | 131.4636 | 142.756 | 139.9609 | 748.9201 | 877.2177 | 895.3084 | 671.1041 | 5.0293
2024-12-12 | 45639 | 335.7449 | 0.61538 | 62.0696 | 3.6817 | 47.9313 | 0.99136 | 0 | 0 | 1356.7717 | 4.5405 | 4.5028 | 116.8786 | 113.9354 | 102.0947 | 121.5586 | 132.2676 | 129.7153 | 583.512 | 668.2017 | 799.3199 | 557.4801 | 0.093696
2024-12-13 | 45639.0417 | 316.4525 | 0.63224 | 62.7036 | 0.15022 | 52.1809 | 0 | 0 | 0 | 1357.8423 | 4.8836 | 4.7185 | 115.4544 | 112.2336 | 100.7785 | 116.8137 | 127.6639 | 124.7762 | 585.2404 | 656.2644 | 804.9587 | 552.8971 | -0.082357
2024-12-13 | 45639.0833 | 311.8923 | 0.64192 | 62.072 | 0 | 51.073 | 1.084 | 0 | 0 | 1360.6235 | 4.9819 | 4.7164 | 115.0752 | 111.8668 | 100.5459 | 115.1187 | 126.0138 | 123.0052 | 587.6043 | 648.6249 | 807.2055 | 553.4959 | 1.6568
2024-12-13 | 45639.125 | 308.0209 | 0.64978 | 56.4775 | 0 | 46.5871 | 0 | 0 | 0 | 1360.8323 | 4.9543 | 4.6288 | 114.4277 | 111.412 | 100.0006 | 113.8679 | 124.9522 | 122.0513 | 587.3854 | 641.8051 | 808.2557 | 552.5342 | 2.4697
2024-12-13 | 45639.1667 | 307.8893 | 0.64934 | 56.8671 | 0 | 46.1073 | 0 | 0 | 0 | 1362.7386 | 4.8246 | 4.6317 | 114.0494 | 111.3649 | 99.4287 | 113.2207 | 124.2942 | 121.5529 | 591.3096 | 640.6176 | 811.3419 | 551.3972 | 1.1383
2024-12-13 | 45639.2083 | 324.7401 | 0.65743 | 61.3065 | 1.3446 | 46.7592 | 0.65701 | 6.6682 | 2.2082 | 1415.3164 | 4.6171 | 4.7041 | 114.581 | 112.187 | 99.3028 | 113.0452 | 124.1937 | 121.8045 | 642.8825 | 692.249 | 824.7425 | 590.5455 | 0.41734
2024-12-13 | 45639.25 | 501.9377 | 0.65366 | 109.9406 | 14.3923 | 86.4907 | 10.6448 | 31.9145 | 23.4399 | 1909.0615 | 3.9199 | 3.7614 | 128.9336 | 123.9977 | 108.7247 | 127.3139 | 140.1176 | 137.3651 | 1066.8198 | 1161.3822 | 1029.2848 | 879.7664 | 3.0985
2024-12-13 | 45639.2917 | 558.9778 | 0.63219 | 109.8521 | 9.5484 | 87.117 | 5.6251 | 23.7699 | 11.8236 | 1977.4666 | 3.2405 | 3.4934 | 131.4359 | 126.2998 | 110.6782 | 136.5423 | 149.1906 | 146.0581 | 1129.7131 | 1301.7439 | 1109.5156 | 867.9389 | 10.2036
2024-12-13 | 45639.3333 | 573.1655 | 0.61964 | 111.3671 | 7.9017 | 100.2028 | 3.5968 | 29.5396 | 14.3086 | 2081.0242 | 3.2876 | 2.7757 | 130.321 | 124.9829 | 109.9219 | 138.3137 | 150.7161 | 147.1714 | 1179.4948 | 1392.8844 | 1202.6879 | 878.3344 | 17.0862
2024-12-13 | 45639.375 | 578.3177 | 0.62442 | 113.0908 | 5.6616 | 108.5354 | 1.9385 | 37.8182 | 7.2065 | 2122.2031 | 3.9186 | 2.699 | 130.1801 | 124.1633 | 109.5552 | 137.5818 | 151.3839 | 146.9863 | 1221.6 | 1470.75 | 1277.7649 | 844.4646 | 28.5088
2024-12-13 | 45639.4167 | 577.0555 | 0.61962 | 110.127 | 5.6527 | 99.4248 | 13.0371 | 37.4305 | 9.4505 | 2002.8663 | 3.5564 | 3.553 | 130.7525 | 125.2722 | 110.6509 | 139.6031 | 152.5258 | 148.8774 | 1115.762 | 1356.2454 | 1174.8937 | 828.0031 | 23.2189
2024-12-13 | 45639.4583 | 580.3903 | 0.61894 | 116.0837 | 11.2413 | 108.3571 | 14.2624 | 39.1504 | 26.4166 | 1956.3191 | 3.3915 | 3.3557 | 132.0034 | 127.4231 | 112.1879 | 141.581 | 154.0579 | 150.7405 | 1087.0901 | 1316.2599 | 1132.715 | 823.617 | 16.5035
2024-12-13 | 45639.5 | 583.0739 | 0.61541 | 103.3911 | 10.3885 | 91.8489 | 12.8426 | 39.0668 | 33.4678 | 1965.223 | 3.5051 | 3.2714 | 133.5012 | 129.9345 | 113.7924 | 142.503 | 154.8738 | 151.8428 | 1105.9386 | 1329.803 | 1140.5546 | 824.6437 | 18.421
2024-12-13 | 45639.5417 | 579.2399 | 0.61836 | 105.7068 | 15.1572 | 83.8728 | 11.7721 | 38.4802 | 34.0914 | 1954.6002 | 3.2102 | 3.4418 | 135.237 | 131.4506 | 115.4552 | 144.731 | 155.2508 | 153.721 | 1095.3881 | 1332.212 | 1131.6866 | 822.9069 | 12.661
2024-12-13 | 45639.5833 | 523.702 | 0.58549 | 96.9775 | 9.2637 | 77.0435 | 6.8754 | 30.6642 | 19.5983 | 1815.5837 | 3.6562 | 3.7625 | 131.8662 | 128.6185 | 113.3966 | 142.3234 | 154.0127 | 151.6483 | 953.4566 | 1173.3292 | 1041.4709 | 774.103 | 16.5436
2024-12-13 | 45639.625 | 474.8113 | 0.63936 | 107.377 | 7.3651 | 104.4584 | 13.029 | 42.6068 | 9.6081 | 1744.6213 | 3.8832 | 3.6475 | 129.105 | 125.6638 | 111.2646 | 134.1324 | 145.4925 | 143.3924 | 880.7731 | 1041.8607 | 975.0615 | 769.5919 | 7.3205
2024-12-13 | 45639.6667 | 574.1557 | 0.61272 | 109.7542 | 10.4066 | 97.2103 | 11.5923 | 44.1729 | 26.5761 | 1991.9188 | 3.5354 | 3.5674 | 135.4283 | 131.264 | 115.463 | 140.3278 | 152.7615 | 150.2676 | 1113.3226 | 1306.0182 | 1119.066 | 872.8524 | 37.235
2024-12-13 | 45639.7083 | 576.8265 | 0.61004 | 114.2044 | 8.9023 | 112.1334 | 15.4923 | 39.4712 | 13.6363 | 2003.9222 | 3.9822 | 3.5416 | 136.5317 | 132.4651 | 116.4179 | 141.5026 | 154.1815 | 152.0255 | 1132.5304 | 1357.6222 | 1143.3947 | 860.5261 | 35.6949
2024-12-13 | 45639.75 | 574.114 | 0.61341 | 135.3537 | 12.0045 | 112.4145 | 14.7534 | 21.8076 | 0 | 1992.2701 | 4.0181 | 3.4857 | 132.6885 | 128.9783 | 112.9521 | 140.9361 | 153.799 | 151.7197 | 1085.3702 | 1356.2306 | 1135.7155 | 856.5715 | 16.2803
2024-12-13 | 45639.7917 | 543.0468 | 0.60533 | 110.1862 | 18.2804 | 82.592 | 14.401 | 15.3318 | 0 | 1897.427 | 4.1095 | 3.8272 | 129.527 | 126.2334 | 110.2984 | 139.498 | 151.0354 | 149.6608 | 1010.4214 | 1263.8008 | 1100.661 | 796.7182 | 11.5062
2024-12-13 | 45639.8333 | 548.9886 | 0.61314 | 126.4385 | 18.2395 | 107.4808 | 19.1008 | 23.1818 | 0.39316 | 1904.2592 | 3.6394 | 3.6435 | 128.782 | 125.1036 | 109.6766 | 137.8836 | 149.6535 | 147.8071 | 1011.641 | 1243.5682 | 1083.0736 | 821.1589 | 10.1191
2024-12-13 | 45639.875 | 576.2877 | 0.60379 | 127.1207 | 22.4736 | 96.5898 | 16.8185 | 28.2487 | 5.7839 | 1970.7703 | 3.884 | 3.5279 | 130.6664 | 126.3593 | 110.6871 | 137.6469 | 150.399 | 147.9001 | 1080.5131 | 1315.9265 | 1136.0609 | 834.723 | 12.0166
2024-12-13 | 45639.9167 | 552.4506 | 0.60312 | 118.8539 | 22.6572 | 91.0171 | 17.4125 | 28.8611 | 12.5478 | 1916.2026 | 3.9019 | 3.693 | 128.9109 | 124.9983 | 109.2879 | 137.4037 | 150.1065 | 147.7333 | 1022.694 | 1257.4767 | 1082.3005 | 833.8916 | 12.1285
2024-12-13 | 45639.9583 | 490.9861 | 0.5945 | 106.994 | 17.473 | 80.0323 | 15.9398 | 24.4147 | 6.1172 | 1744.6865 | 4.0172 | 3.561 | 126.3761 | 123.1957 | 108.0521 | 134.6265 | 146.7054 | 144.2212 | 882.4094 | 1080.8962 | 1012.416 | 732.3102 | 9.6891
2024-12-13 | 45640 | 336.0986 | 0.60908 | 64.3637 | 3.1716 | 54.4794 | 7.5475 | 4.0443 | 0.24209 | 1331.9655 | 4.1628 | 4.2676 | 114.0435 | 112.604 | 99.7124 | 122.9445 | 133.5406 | 131.4903 | 553.1205 | 677.7579 | 795.0034 | 536.9233 | 2.5706
2024-12-14 | 45640.0417 | 367.212 | 0.64416 | 85.8261 | 10.2557 | 78.3503 | 16.2796 | 16.1985 | 4.0221 | 1425.5557 | 4.2086 | 3.6308 | 119.0111 | 116.1192 | 103.7893 | 118.3451 | 129.4305 | 126.7626 | 619.5726 | 710.2129 | 781.1882 | 644.3583 | 0.18457
2024-12-14 | 45640.0833 | 339.5547 | 0.64149 | 80.8248 | 4.4763 | 65.0469 | 7.7108 | 4.3027 | 0 | 1363.4004 | 4.2586 | 3.9584 | 119.4191 | 117.3567 | 104.993 | 118.6138 | 129.7084 | 126.9878 | 592.9667 | 684.7243 | 789.2704 | 574.183 | -0.040988
2024-12-14 | 45640.125 | 315.4777 | 0.64216 | 71.5532 | 6.6086 | 56.6328 | 6.3219 | 0 | 0 | 1341.2035 | 4.3869 | 3.909 | 114.3245 | 112.6062 | 100.0039 | 116.7239 | 127.5839 | 125.0224 | 565.828 | 668.6002 | 794.5804 | 546.6417 | -0.15705
2024-12-14 | 45640.1667 | 317.7832 | 0.63756 | 73.5552 | 5.0807 | 57.6257 | 2.9775 | 0 | 0 | 1345.2349 | 4.3585 | 3.4878 | 113.6177 | 111.7196 | 99.1435 | 115.9577 | 126.9177 | 124.2827 | 571.5546 | 669.677 | 796.6863 | 548.5452 | 0.078635
2024-12-14 | 45640.2083 | 362.7909 | 0.65203 | 86.3121 | 9.2894 | 78.4795 | 15.6892 | 20.0935 | 5.7297 | 1466.4675 | 4.2496 | 3.2224 | 117.9125 | 114.8728 | 102.0368 | 116.7738 | 128.1145 | 125.2968 | 667.5945 | 760.0078 | 821.1478 | 645.3023 | -0.26092
2024-12-14 | 45640.25 | 551.3519 | 0.63865 | 138.4761 | 12.1559 | 123.1372 | 36.6752 | 37.745 | 17.2974 | 1950.1198 | 3.5193 | 3.3623 | 132.6833 | 128.2645 | 112.2039 | 129.2702 | 142.0166 | 138.7111 | 1108.8279 | 1270.1471 | 1116.7648 | 833.3282 | 3.8476
2024-12-14 | 45640.2917 | 576.8747 | 0.61279 | 118.4679 | 9.3147 | 90.5586 | 12.9029 | 20.9391 | 4.0945 | 1993.5892 | 3.4224 | 2.6182 | 130.8879 | 126.8928 | 110.5724 | 133.1045 | 145.9406 | 142.7997 | 1129.7958 | 1351.3788 | 1182.8429 | 810.7721 | 8.4701
2024-12-14 | 45640.3333 | 577.4561 | 0.6102 | 121.2294 | 6.1025 | 98.2879 | 12.3661 | 27.4479 | 0 | 1996.054 | 3.4877 | 3.4482 | 129.4374 | 125.794 | 109.5481 | 134.5771 | 146.4827 | 143.9557 | 1117.0352 | 1367.9402 | 1175.869 | 820.1716 | 10.5484
2024-12-14 | 45640.375 | 577.3523 | 0.61563 | 134.9013 | 8.7415 | 106.2747 | 17.3484 | 29.2433 | 1.8593 | 1954.0504 | 3.3063 | 3.5331 | 130.1159 | 126.2903 | 110.3546 | 135.5249 | 148.3624 | 145.453 | 1073.4033 | 1322.0121 | 1140.2478 | 813.8127 | 9.9486
2024-12-14 | 45640.4167 | 578.2274 | 0.61026 | 137.8544 | 10.342 | 106.6496 | 16.2268 | 30.3648 | 0.070714 | 1939.2323 | 3.2024 | 3.4875 | 130.9988 | 127.2911 | 111.4336 | 137.7749 | 150.3413 | 147.4839 | 1053.7101 | 1310.5441 | 1131.2577 | 807.9475 | 9.2641
2024-12-14 | 45640.4583 | 575.0993 | 0.60585 | 137.2619 | 12.7705 | 110.4391 | 21.7497 | 32.7401 | 6.1743 | 1922.2814 | 3.3053 | 3.4312 | 132.2894 | 128.5346 | 112.7781 | 139.8057 | 152.2752 | 149.5252 | 1038.839 | 1298.8899 | 1111.5996 | 810.6595 | 10.3953
2024-12-14 | 45640.5 | 509.9141 | 0.61708 | 124.7151 | 13.3356 | 98.2853 | 25.9822 | 23.9077 | 7.5259 | 1771.1276 | 3.3856 | 3.7633 | 131.3243 | 128.5122 | 113.1111 | 139.2296 | 150.892 | 148.647 | 898.5834 | 1125.7825 | 1018.3622 | 752.7549 | 9.608
2024-12-14 | 45640.5417 | 510.6285 | 0.63007 | 133.413 | 17.032 | 104.6086 | 34.2262 | 30.127 | 10.8598 | 1795.002 | 3.6727 | 3.7471 | 132.1434 | 128.6193 | 113.4741 | 136.3015 | 148.056 | 145.6222 | 957.0215 | 1160.0066 | 1055.9041 | 739.0824 | 9.677
2024-12-14 | 45640.5833 | 526.3535 | 0.626 | 138.3096 | 14.1234 | 92.1392 | 23.1017 | 26.9951 | 6.3319 | 1863.9248 | 3.7494 | 3.8779 | 133.2935 | 129.7451 | 114.4912 | 137.4334 | 149.4445 | 146.9462 | 1006.1239 | 1238.5552 | 1109.2974 | 754.5781 | 12.3055
2024-12-14 | 45640.625 | 532.1327 | 0.61891 | 135.3615 | 13.7604 | 96.4723 | 24.0202 | 31.3598 | 8.7083 | 1905.7528 | 4.0304 | 3.8517 | 133.6526 | 129.6764 | 114.6417 | 138.0056 | 150.1008 | 147.4845 | 1039.0544 | 1275.3105 | 1150.5369 | 755.2034 | 13.7543
2024-12-14 | 45640.6667 | 575.2023 | 0.61756 | 146.74 | 11.967 | 111.8127 | 14.2281 | 31.7764 | 19.4001 | 2006.5852 | 3.5755 | 3.8504 | 134.6617 | 130.6716 | 115.1391 | 140.9989 | 153.4087 | 151.0637 | 1105.0713 | 1381.7294 | 1141.7219 | 864.866 | 13.7132
2024-12-14 | 45640.7083 | 585.4144 | 0.61301 | 142.4203 | 27.5959 | 106.7372 | 22.3413 | 39.5028 | 31.2444 | 1998.4648 | 3.5938 | 3.7172 | 134.9273 | 131.0718 | 115.2989 | 141.706 | 154.2554 | 152.03 | 1099.7799 | 1379.0435 | 1153.1864 | 845.2866 | 9.8185
2024-12-14 | 45640.75 | 586.19 | 0.61354 | 145.0536 | 26.0081 | 107.589 | 9.6389 | 36.7123 | 31.7101 | 2003.2749 | 3.2958 | 3.7013 | 134.7061 | 130.6752 | 114.7089 | 141.5533 | 153.9794 | 151.5065 | 1106.6895 | 1384.178 | 1158.8787 | 844.3648 | 10.3732
2024-12-14 | 45640.7917 | 589.1795 | 0.61019 | 143.0933 | 24.5572 | 117.9737 | 15.2388 | 40.3105 | 35.287 | 2019.4404 | 3.0741 | 3.6676 | 134.2506 | 129.942 | 113.9544 | 140.7003 | 153.5808 | 150.517 | 1128.9868 | 1406.9741 | 1174.6204 | 844.8199 | 9.5461
2024-12-14 | 45640.8333 | 584.1188 | 0.59843 | 121.3142 | 14.9586 | 97.9955 | 7.6819 | 31.3891 | 22.3563 | 2025.3336 | 3.2235 | 3.8023 | 132.0154 | 127.9587 | 111.7685 | 140.1247 | 153.1045 | 150.1658 | 1115.1884 | 1412.4996 | 1175.9183 | 849.4427 | 10.9328
2024-12-14 | 45640.875 | 579.5473 | 0.60122 | 102.77 | 20.9974 | 88.4542 | 14.708 | 28.343 | 19.2592 | 1988.3345 | 3.1354 | 3.8272 | 131.1224 | 127.5223 | 110.9563 | 140.4393 | 151.8258 | 150.1392 | 1086.8717 | 1376.6537 | 1137.1469 | 851.1898 | 8.3131
2024-12-14 | 45640.9167 | 530.4604 | 0.59564 | 99.3607 | 10.7783 | 87.0779 | 18.3743 | 23.8986 | 5.7167 | 1881.5197 | 3.9269 | 3.9851 | 127.2925 | 123.7764 | 108.1497 | 134.6463 | 147.4448 | 144.628 | 984.0279 | 1241.0355 | 1116.3496 | 765.1839 | 10.7018
2024-12-14 | 45640.9583 | 521.9285 | 0.60506 | 111.4999 | 12.1725 | 89.4916 | 25.3981 | 21.2848 | 0.19234 | 1858.3087 | 3.7679 | 3.5701 | 127.1967 | 123.2069 | 107.8354 | 131.1634 | 143.6206 | 140.3096 | 986.232 | 1197.2898 | 1109.5708 | 748.7443 | 8.8669
2024-12-14 | 45641 | 482.1118 | 0.58544 | 99.633 | 8.5975 | 76.4209 | 20.9453 | 24.7298 | 0 | 1706.0829 | 4.0097 | 3.5222 | 127.4006 | 124.0681 | 109.134 | 129.4845 | 141.6316 | 138.429 | 873.1391 | 1046.7179 | 1017.4976 | 688.6898 | 7.1514
2024-12-15 | 45641.0417 | 342.1712 | 0.60171 | 60.8639 | 5.337 | 43.165 | 5.6128 | 0 | 0 | 1355.6823 | 4.0435 | 4.2836 | 115.305 | 114.1845 | 100.8585 | 120.6357 | 131.3394 | 128.9791 | 568.3135 | 689.5543 | 805.7037 | 549.9693 | 0.82456
2024-12-15 | 45641.0833 | 328.1619 | 0.61424 | 61.0364 | 0.56672 | 49.9356 | 7.2163 | 0 | 0 | 1356.92 | 4.3729 | 4.3876 | 113.5034 | 111.792 | 98.8655 | 115.5696 | 126.4996 | 123.7584 | 574.2938 | 665.7595 | 802.4581 | 554.4418 | -0.087283
2024-12-15 | 45641.125 | 321.6676 | 0.62206 | 63.7197 | 4.5092 | 51.3755 | 6.7925 | 0 | 0 | 1357.6033 | 4.485 | 4.437 | 114.0324 | 111.5717 | 99.3442 | 113.5731 | 124.481 | 121.8844 | 577.741 | 656.3484 | 802.293 | 555.3069 | 0.18058
2024-12-15 | 45641.1667 | 317.8459 | 0.63161 | 62.8883 | 4.6525 | 54.9158 | 5.7622 | 0 | 0 | 1355.2036 | 4.4458 | 4.3747 | 114.054 | 111.5486 | 99.4691 | 112.3214 | 123.1032 | 120.6584 | 576.8815 | 647.9548 | 801.8201 | 553.4067 | 0.066954
2024-12-15 | 45641.2083 | 349.3566 | 0.6476 | 80.2096 | 10.3889 | 71.589 | 13.1079 | 12.573 | 4.832 | 1424.8469 | 4.3715 | 3.266 | 116.5607 | 113.8187 | 101.3918 | 113.544 | 124.7258 | 121.9184 | 634.3486 | 704.3998 | 810.9922 | 613.859 | 0.717
2024-12-15 | 45641.25 | 484.256 | 0.61522 | 116.1572 | 15.1441 | 106.8918 | 27.3418 | 15.7064 | 7.2331 | 1733.9398 | 3.7047 | 3.0307 | 127.56 | 123.7345 | 109.0347 | 123.3602 | 135.6692 | 132.3727 | 915.7111 | 1018.8879 | 990.1157 | 743.7891 | 0.043012
2024-12-15 | 45641.2917 | 521.4188 | 0.6108 | 108.0664 | 11.7143 | 100.0301 | 23.2463 | 21.3929 | 2.9889 | 1804.4631 | 3.4686 | 2.5292 | 130.1657 | 126.6398 | 110.9797 | 126.7369 | 137.8303 | 135.3666 | 990.4435 | 1100.2206 | 1009.8063 | 794.6738 | 0.15543
2024-12-15 | 45641.3333 | 517.4072 | 0.60205 | 115.4168 | 9.0766 | 101.5564 | 14.6965 | 23.9353 | 0 | 1959.0935 | 4.1094 | 2.2606 | 128.2339 | 124.133 | 108.806 | 127.3207 | 139.8723 | 136.1961 | 1086.7311 | 1259.3567 | 1179.7262 | 779.3052 | 6.8412
2024-12-15 | 45641.375 | 573.534 | 0.59822 | 114.9458 | 9.3812 | 103.2202 | 10.4595 | 24.8065 | 1.9012 | 2119.8125 | 3.885 | 2.5798 | 130.3114 | 125.3932 | 109.8022 | 132.9675 | 146.5196 | 142.6478 | 1226.4459 | 1473.028 | 1275.3221 | 844.5291 | 12.6617
2024-12-15 | 45641.4167 | 581.0262 | 0.59381 | 108.2337 | 8.7227 | 90.8219 | 17.1728 | 32.473 | 0 | 2022.7661 | 3.6197 | 3.8072 | 131.1704 | 126.6212 | 111.0727 | 136.0756 | 148.8362 | 145.643 | 1143.2384 | 1388.7194 | 1189.3997 | 833.3604 | 10.872
2024-12-15 | 45641.4583 | 576.3278 | 0.59764 | 119.1205 | 12.7154 | 97.7941 | 22.8337 | 33.2797 | 0 | 1912.103 | 3.3236 | 3.4705 | 132.4531 | 128.5713 | 113.0173 | 138.0715 | 150.3192 | 147.601 | 1049.3124 | 1287.2292 | 1094.7012 | 817.4004 | 11.5176
2024-12-15 | 45641.5 | 580.0606 | 0.59409 | 133.6308 | 15.5082 | 99.7549 | 20.8201 | 27.9167 | 1.9545 | 1908.2365 | 3.0646 | 3.3944 | 134.0329 | 130.169 | 114.4556 | 138.926 | 151.1999 | 148.4326 | 1055.3783 | 1280.4857 | 1101.1735 | 807.0623 | 7.6967
2024-12-15 | 45641.5417 | 582.0023 | 0.59038 | 124.1957 | 16.7162 | 96.994 | 19.9447 | 29.8441 | 7.9492 | 1881.4373 | 2.9221 | 3.339 | 134.4581 | 130.7321 | 114.8992 | 139.6259 | 151.4534 | 148.8803 | 1037.5221 | 1255.0925 | 1072.4601 | 808.9753 | 6.0771
2024-12-15 | 45641.5833 | 576.0829 | 0.5956 | 120.7047 | 18.4345 | 94.68 | 19.7044 | 25.7564 | 10.6831 | 1872.7855 | 2.8179 | 3.4834 | 135.0943 | 131.6388 | 115.6676 | 139.8122 | 151.5345 | 149.2034 | 1031.0272 | 1247.3473 | 1070.4827 | 802.2986 | 4.5102
2024-12-15 | 45641.625 | 571.8692 | 0.61108 | 124.16 | 14.2436 | 95.6677 | 21.3621 | 31.0741 | 13.3734 | 1870.1527 | 2.9745 | 3.2679 | 137.2051 | 133.83 | 117.6494 | 140.5191 | 150.6161 | 149.3348 | 1053.0214 | 1246.4712 | 1075.9629 | 794.1822 | 2.4233
2024-12-15 | 45641.6667 | 565.6706 | 0.59162 | 124.3205 | 12.7269 | 90.8303 | 12.6927 | 31.1792 | 20.0053 | 1897.6213 | 2.9168 | 3.5301 | 136.4986 | 132.7633 | 117.1916 | 139.782 | 151.4758 | 148.9098 | 1052.5928 | 1265.0317 | 1108.0823 | 789.554 | 5.406
2024-12-15 | 45641.7083 | 433.4955 | 0.60879 | 104.1283 | 10.0619 | 80.1619 | 11.0471 | 11.8032 | 2.8444 | 1603.0109 | 3.4661 | 4.0266 | 129.168 | 126.8806 | 112.5126 | 133.4133 | 144.1303 | 141.9808 | 770.4704 | 917.4788 | 901.97 | 701.0157 | 3.0802
2024-12-15 | 45641.75 | 547.9841 | 0.61152 | 118.9711 | 8.3019 | 100.8837 | 13.5829 | 29.2616 | 16.481 | 1958.6196 | 3.5368 | 3.7319 | 135.9019 | 131.5396 | 116.0747 | 134.5983 | 146.696 | 143.6116 | 1107.6743 | 1272.2455 | 1139.0869 | 819.5213 | 4.0209
2024-12-15 | 45641.7917 | 582.569 | 0.58912 | 119.0159 | 9.2083 | 97.0482 | 10.4884 | 31.7054 | 6.912 | 1979.9475 | 3.6628 | 3.4528 | 137.7868 | 133.5602 | 117.3621 | 137.6477 | 150.185 | 147.3066 | 1133.8954 | 1316.6387 | 1123.1824 | 856.7877 | 7.7047
2024-12-15 | 45641.8333 | 549.1541 | 0.58246 | 117.027 | 10.8507 | 90.3255 | 21.2812 | 31.9638 | 15.0996 | 1855.7426 | 3.6256 | 3.6505 | 135.6164 | 131.9912 | 115.9399 | 137.1133 | 149.3471 | 146.7931 | 1023.0209 | 1204.2499 | 1061.8566 | 793.8622 | 6.5848
2024-12-15 | 45641.875 | 554.8556 | 0.58548 | 134.5109 | 16.1474 | 94.106 | 20.9433 | 38.7438 | 11.7027 | 1868.7909 | 3.5576 | 3.4511 | 133.6167 | 129.3959 | 113.7382 | 132.7631 | 145.0672 | 141.9708 | 1039.3955 | 1200.876 | 1123.903 | 744.8823 | 1.5844
2024-12-15 | 45641.9167 | 496.151 | 0.5845 | 119.6843 | 16.8902 | 83.0817 | 19.3045 | 30.639 | 1.2221 | 1726.1729 | 3.8353 | 3.6948 | 132.034 | 129.0593 | 113.2814 | 132.7003 | 142.7125 | 140.9505 | 918.7488 | 1052.767 | 985.0142 | 741.2163 | 1.3583
2024-12-15 | 45641.9583 | 410.557 | 0.59115 | 89.3253 | 6.6334 | 63.5976 | 12.6372 | 6.5521 | 0 | 1551.7788 | 4.5135 | 4.2849 | 127.6567 | 125.7804 | 111.0076 | 126.5249 | 136.1742 | 134.5348 | 761.5511 | 866.084 | 903.2651 | 648.5164 | 0.025326
2024-12-15 | 45642 | 324.5246 | 0.62082 | 54.2418 | 5.7974 | 38.6793 | 7.4272 | 0.69075 | 0.24829 | 1359.8113 | 4.3463 | 4.4639 | 117.831 | 116.9318 | 103.6721 | 117.377 | 127.5805 | 125.6588 | 593.7169 | 674.3169 | 812.9256 | 546.8882 | 1.4217
2024-12-16 | 45642.0417 | 320.3152 | 0.62754 | 55.0693 | 9.1356 | 37.5135 | 5.0625 | 0.41206 | 0.32875 | 1364.2284 | 4.4026 | 4.53 | 116.4302 | 115.1149 | 102.0776 | 114.5637 | 125.3968 | 122.7121 | 596.6578 | 661.0252 | 807.9689 | 556.2665 | 0.284
2024-12-16 | 45642.0833 | 322.6522 | 0.62559 | 60.1847 | 10.2233 | 42.1786 | 6.0147 | 0 | 0 | 1362.3207 | 4.3595 | 4.5274 | 117.0448 | 115.7505 | 102.5224 | 114.1491 | 124.8813 | 122.1611 | 605.704 | 662.2615 | 807.2864 | 555.0384 | -0.040788
2024-12-16 | 45642.125 | 320.8216 | 0.62413 | 60.5768 | 10.0023 | 43.5036 | 5.9093 | 0 | 0 | 1359.7638 | 4.4207 | 4.5173 | 117.2302 | 116.0422 | 102.8341 | 113.8122 | 124.5326 | 122.0583 | 607.6782 | 660.7612 | 806.2448 | 553.5472 | -0.12113
2024-12-16 | 45642.1667 | 325.0669 | 0.62243 | 69.9256 | 5.3671 | 52.7625 | 2.8151 | 9.8085 | 1.9816 | 1389.9437 | 4.532 | 3.0115 | 118.2379 | 117.033 | 103.7269 | 114.1865 | 125.0002 | 122.4156 | 625.0006 | 675.7589 | 805.8462 | 584.0914 | -0.15819
2024-12-16 | 45642.2083 | 322.8648 | 0.62058 | 61.4265 | 12.2717 | 42.9881 | 10.6466 | 0.024108 | 0 | 1351.8041 | 4.6374 | 2.2255 | 117.9881 | 116.7791 | 103.5262 | 113.0085 | 124.0729 | 121.2865 | 619.0099 | 665.512 | 817.4371 | 534.3664 | -0.060129
2024-12-16 | 45642.25 | 413.543 | 0.63512 | 97.6451 | 13.0271 | 85.3744 | 15.0275 | 17.5965 | 9.3564 | 1720.557 | 4.305 | 2.5927 | 123.9596 | 120.3474 | 106.1486 | 117.8082 | 129.4746 | 126.0757 | 925.8006 | 996.6449 | 1036.694 | 683.8746 | 0.7066
2024-12-16 | 45642.2917 | 562.5887 | 0.59749 | 139.1315 | 9.7894 | 117.7018 | 13.6517 | 19.1383 | 5.7196 | 2003.1093 | 3.5645 | 2.6429 | 132.7763 | 128.1138 | 112.2757 | 129.3507 | 142.3283 | 138.675 | 1188.6415 | 1320.3782 | 1170.0709 | 833.0453 | 0.42574
2024-12-16 | 45642.3333 | 578.9504 | 0.5823 | 129.5098 | 6.9885 | 116.5281 | 11.1264 | 19.58 | 4.0408 | 2026.7208 | 3.5926 | 2.3441 | 132.2491 | 127.6887 | 111.8606 | 131.6332 | 144.8212 | 141.2114 | 1182.4709 | 1357.4559 | 1213.7614 | 812.9709 | 4.8811
2024-12-16 | 45642.375 | 572.6194 | 0.58074 | 105.7677 | 8.3106 | 96.8518 | 12.3808 | 12.1148 | 0 | 1973.2046 | 3.3861 | 2.8291 | 131.0238 | 126.7608 | 110.9714 | 135.1137 | 146.8175 | 144.0768 | 1128.1671 | 1327.2921 | 1167.6005 | 805.5909 | 4.5135
2024-12-16 | 45642.4167 | 571.8071 | 0.58003 | 117.3732 | 11.6301 | 97.7433 | 15.0069 | 17.4979 | 0.75346 | 1916.5476 | 2.7173 | 3.4711 | 132.6511 | 128.563 | 112.8165 | 137.0771 | 149.0423 | 146.3657 | 1090.9139 | 1272.3312 | 1142.1891 | 774.349 | 2.6579
2024-12-16 | 45642.4583 | 571.9642 | 0.57883 | 115.4158 | 8.7974 | 88.4037 | 16.8936 | 21.3948 | 0 | 1915.791 | 3.15 | 3.1613 | 133.4919 | 129.0281 | 113.5009 | 135.2334 | 147.5319 | 144.4985 | 1102.35 | 1271.6923 | 1186.3704 | 729.4236 | 2.9782
2024-12-16 | 45642.5 | 566.5257 | 0.57599 | 120.3295 | 8.9482 | 97.6639 | 17.8375 | 23.9085 | 0 | 1895.3307 | 3.1152 | 3.1806 | 134.0806 | 129.7046 | 114.232 | 135.6725 | 147.4079 | 144.9378 | 1090.4185 | 1249.1298 | 1165.469 | 729.845 | 2.0396
2024-12-16 | 45642.5417 | 510.0617 | 0.55007 | 116.073 | 9.3536 | 85.1498 | 10.8199 | 10.6502 | 0.4486 | 1746.8503 | 3.3801 | 3.7467 | 132.493 | 128.8138 | 113.9371 | 134.8891 | 145.8179 | 143.611 | 961.3262 | 1098.1567 | 1083.4879 | 663.3763 | 1.9849
2024-12-16 | 45642.5833 | 392.319 | 0.59328 | 81.846 | 7.3148 | 57.0622 | 10.5373 | 12.476 | 1.2868 | 1468.8879 | 4.271 | 3.8094 | 125.3149 | 122.4152 | 109.9111 | 124.9633 | 135.3964 | 133.2048 | 697.2465 | 777.6496 | 869.8752 | 599.0086 | 0.68394
2024-12-16 | 45642.625 | 558.3772 | 0.58697 | 121.8933 | 8.9017 | 99.307 | 13.2128 | 30.0786 | 3.4629 | 1947.0928 | 3.5498 | 3.3185 | 135.7477 | 130.4736 | 115.9261 | 132.8554 | 144.2751 | 141.8279 | 1133.1138 | 1253.9353 | 1198.6265 | 748.4792 | 2.5917
2024-12-16 | 45642.6667 | 583.9363 | 0.56097 | 115.2383 | 5.5207 | 83.3027 | 15.4099 | 30.0064 | 0 | 2002.7633 | 3.6454 | 3.5067 | 136.5538 | 131.6868 | 116.4426 | 136.4462 | 148.3497 | 145.6695 | 1176.7885 | 1350.9204 | 1250.9885 | 751.759 | 7.7021
2024-12-16 | 45642.7083 | 580.6387 | 0.55661 | 111.9396 | 5.484 | 91.4042 | 16.3515 | 28.2957 | 0 | 1981.803 | 3.4883 | 3.5142 | 135.6157 | 130.736 | 115.5077 | 136.9268 | 148.8037 | 145.906 | 1151.1442 | 1329.337 | 1235.3253 | 746.4589 | 6.6888
2024-12-16 | 45642.75 | 571.2028 | 0.55466 | 122.1896 | 5.6234 | 92.9746 | 15.8115 | 27.2596 | 0 | 1941.9161 | 3.3846 | 3.4944 | 134.4305 | 129.6266 | 114.3966 | 135.7306 | 147.8031 | 144.5337 | 1112.429 | 1284.4072 | 1205.4581 | 736.4662 | 5.4795
2024-12-16 | 45642.7917 | 575.757 | 0.55267 | 122.7244 | 7.5999 | 89.1597 | 14.2138 | 29.0299 | 0 | 1945.4524 | 3.2528 | 3.4506 | 133.8813 | 128.907 | 113.455 | 135.1578 | 147.3822 | 143.9898 | 1123.7095 | 1290.6252 | 1212.4166 | 733.0154 | 3.9116
2024-12-16 | 45642.8333 | 571.036 | 0.5565 | 103.7317 | 6.8395 | 67.5301 | 12.4158 | 21.1446 | 0 | 1929.0741 | 3.3258 | 3.4052 | 133.0092 | 128.132 | 112.6923 | 133.9589 | 146.0169 | 142.5139 | 1115.1914 | 1269.7185 | 1200.1448 | 728.9371 | 2.1718
2024-12-16 | 45642.875 | 575.147 | 0.56293 | 100.2664 | 5.7378 | 66.8116 | 13.5348 | 27.2764 | 0 | 1932.855 | 3.2703 | 3.3815 | 134.2709 | 129.4911 | 113.6652 | 134.633 | 145.2259 | 142.7226 | 1133.816 | 1281.251 | 1209.3655 | 723.5189 | 0.61456
2024-12-16 | 45642.9167 | 557.4243 | 0.55998 | 109.5497 | 7.9162 | 73.484 | 15.1994 | 22.9873 | 0 | 1881.564 | 3.2001 | 3.5333 | 131.1879 | 126.4958 | 111.0671 | 132.9572 | 145.0944 | 141.5769 | 1067.5927 | 1218.6057 | 1164.7354 | 716.7956 | 1.5638
2024-12-16 | 45642.9583 | 454.3724 | 0.55539 | 88.7157 | 6.2637 | 51.3603 | 7.5161 | 9.5799 | 0 | 1660.3794 | 4.0742 | 4.1433 | 126.532 | 122.9498 | 108.0432 | 127.7532 | 139.3474 | 136.0473 | 868.4763 | 982.8359 | 1021.3205 | 639.0171 | 0.90174
2024-12-16 | 45643 | 330.1928 | 0.59492 | 44.0739 | 5.5308 | 23.7663 | 6.9063 | 0.42055 | 0 | 1360.5615 | 4.6353 | 4.3851 | 117.805 | 116.1424 | 102.4804 | 117.8971 | 128.4922 | 125.7271 | 616.5377 | 686.0704 | 834.2882 | 526.277 | 0.11214
2024-12-17 | 45643.0417 | 322.6425 | 0.61561 | 55.4942 | 4.6177 | 38.0485 | 9.5821 | 8.1095 | 0 | 1320.1418 | 4.506 | 4.1729 | 116.4878 | 114.4685 | 101.6784 | 114.6999 | 125.198 | 122.3653 | 590.497 | 640.373 | 797.0175 | 523.1136 | 0.38788
2024-12-17 | 45643.0833 | 320.7176 | 0.62054 | 59.0286 | 5.5418 | 43.1876 | 9.8796 | 3.4783 | 0 | 1330.5724 | 4.6516 | 4.2629 | 116.9788 | 113.7964 | 102.0744 | 114.2034 | 124.7234 | 122.0769 | 600.8148 | 650.0378 | 799.4433 | 531.1611 | 0.077626
2024-12-17 | 45643.125 | 317.9601 | 0.63012 | 64.9674 | 5.9076 | 48.8497 | 9.9127 | 0 | 0 | 1330.5862 | 4.6875 | 4.2891 | 117.0787 | 113.5579 | 102.1204 | 113.9389 | 124.501 | 121.886 | 598.7643 | 648.0286 | 798.0976 | 532.4833 | -0.078559
2024-12-17 | 45643.1667 | 302.0376 | 0.64883 | 62.4527 | 4.3571 | 48.7771 | 9.2191 | 0 | 0 | 1328.8595 | 4.9481 | 4.5952 | 116.4039 | 113.1311 | 101.6277 | 113.0228 | 123.5398 | 120.895 | 597.3946 | 643.5112 | 797.548 | 531.3143 | -0.11185
2024-12-17 | 45643.2083 | 303.5007 | 0.6594 | 64.2544 | 5.3873 | 51.9772 | 10.2386 | 1.3779 | 0 | 1329.7737 | 4.8734 | 4.4736 | 116.2869 | 112.995 | 101.5172 | 112.4349 | 123.1086 | 120.2665 | 595.4818 | 637.7153 | 799.4003 | 530.3749 | -0.17389
2024-12-17 | 45643.25 | 416.3255 | 0.67865 | 101.9064 | 14.4602 | 97.2881 | 25.9865 | 24.7805 | 5.1031 | 1734.8859 | 4.7881 | 4.2821 | 123.686 | 118.7104 | 105.324 | 117.5323 | 129.4277 | 126.3347 | 941.8018 | 991.2206 | 1005.9149 | 728.9785 | 0.20579
2024-12-17 | 45643.2917 | 565.7358 | 0.62157 | 128.573 | 7.5766 | 122.6328 | 12.9873 | 22.099 | 3.6743 | 2026.8745 | 4.1474 | 3.7193 | 133.7876 | 127.7705 | 111.9484 | 130.7785 | 142.9872 | 140.0629 | 1211.0896 | 1317.7689 | 1178.561 | 848.3051 | -0.18588
2024-12-17 | 45643.3333 | 573.3987 | 0.6263 | 130.6965 | 9.7534 | 115.9118 | 14.3146 | 15.9305 | 0 | 1965.0341 | 3.2487 | 3.5757 | 134.1273 | 128.9754 | 112.6905 | 134.0551 | 146.5551 | 143.1177 | 1163.8892 | 1302.7177 | 1154.218 | 810.8307 | 0.72726
2024-12-17 | 45643.375 | 578.9655 | 0.62534 | 136.6569 | 8.7401 | 132.9715 | 16.844 | 27.2469 | 7.9016 | 1944.3156 | 3.0551 | 3.3537 | 134.7727 | 129.7982 | 113.4024 | 135.3407 | 148.1877 | 144.8193 | 1140.3433 | 1286.7784 | 1139.2406 | 805.0753 | 0.72239
2024-12-17 | 45643.4167 | 578.9436 | 0.62694 | 134.7647 | 9.8902 | 122.5915 | 18.5263 | 31.5032 | 11.5774 | 1951.2322 | 2.6785 | 3.4167 | 136.1761 | 131.3715 | 114.9979 | 137.449 | 150.1318 | 146.8249 | 1141.4418 | 1302.448 | 1150.2173 | 801.0187 | 1.435
2024-12-17 | 45643.4583 | 578.1646 | 0.62807 | 132.285 | 9.4812 | 124.5469 | 18.7585 | 33.4654 | 11.5089 | 1945.6923 | 3.1485 | 3.3587 | 137.0523 | 132.242 | 116.0028 | 139.6633 | 152.0546 | 148.9454 | 1135.2472 | 1313.2386 | 1150.7638 | 794.962 | 4.4899
2024-12-17 | 45643.5 | 578.8312 | 0.62233 | 134.8094 | 10.5012 | 114.9715 | 11.9479 | 30.5086 | 12.6262 | 1948.759 | 3.0948 | 3.4094 | 137.9653 | 133.2087 | 117.1389 | 141.3065 | 153.332 | 150.5703 | 1134.3057 | 1328.7565 | 1147.6777 | 801.0913 | 6.6777
2024-12-17 | 45643.5417 | 558.5063 | 0.62173 | 130.9697 | 13.219 | 110.2263 | 10.1688 | 28.992 | 17.8925 | 1887.9391 | 3.1333 | 3.4678 | 136.6532 | 132.3176 | 116.4516 | 142.3919 | 153.7861 | 151.4922 | 1071.5338 | 1268.5571 | 1092.8828 | 795.0851 | 7.6492
2024-12-17 | 45643.5833 | 462.6832 | 0.63101 | 90.2849 | 10.8618 | 82.5322 | 27.9156 | 6.1702 | 5.8798 | 1592.4236 | 3.7805 | 3.5082 | 133.1268 | 130.3923 | 115.3426 | 134.9242 | 145.739 | 144.0548 | 816.9635 | 925.8594 | 889.0408 | 703.3519 | 2.8915
2024-12-17 | 45643.625 | 506.5578 | 0.65781 | 107.5737 | 11.0093 | 110.2445 | 27.4755 | 9.92 | 0.28068 | 1794.2776 | 3.29 | 3.3675 | 136.7782 | 133.4404 | 117.8659 | 136.3826 | 145.7544 | 144.5742 | 1006.413 | 1119.6553 | 1028.2786 | 766.0256 | 1.2777
2024-12-17 | 45643.6667 | 578.8162 | 0.6352 | 115.5881 | 7.3785 | 112.6498 | 19.0725 | 20.4533 | 6.546 | 1982.6622 | 2.9673 | 3.5199 | 138.2605 | 133.6477 | 117.9963 | 141.7962 | 153.6047 | 151.0984 | 1161.6825 | 1359.8256 | 1174.0725 | 808.5822 | 6.9943
2024-12-17 | 45643.7083 | 583.2494 | 0.62542 | 119.4055 | 9.8145 | 107.198 | 17.9954 | 21.2749 | 8.9445 | 1991.1036 | 2.6773 | 3.5364 | 138.1496 | 133.6745 | 117.8412 | 142.7954 | 154.7758 | 152.2834 | 1161.4805 | 1377.0416 | 1184.6251 | 806.4679 | 8.719
2024-12-17 | 45643.75 | 578.693 | 0.62531 | 121.3127 | 13.4336 | 105.2861 | 21.5404 | 23.2201 | 10.0435 | 1936.2117 | 2.8183 | 3.3187 | 137.2883 | 132.9796 | 116.8932 | 142.2862 | 154.4013 | 151.7596 | 1123.0116 | 1330.3984 | 1142.9581 | 793.2799 | 7.884
2024-12-17 | 45643.7917 | 577.7346 | 0.64537 | 133.2309 | 12.8667 | 115.1612 | 18.4381 | 26.226 | 17.981 | 1970.0885 | 2.9548 | 3.49 | 136.7869 | 132.1784 | 116.0794 | 141.5137 | 153.707 | 150.8777 | 1155.6276 | 1369.9562 | 1185.8904 | 784.1853 | 10.415
2024-12-17 | 45643.8333 | 574.9042 | 0.66329 | 125.5726 | 13.8424 | 110.9868 | 16.0111 | 21.2308 | 13.5974 | 1946.6652 | 2.9178 | 3.4261 | 137.0576 | 132.4369 | 116.0308 | 141.2393 | 153.753 | 150.843 | 1150.834 | 1356.2828 | 1162.4436 | 784.2023 | 8.2571
2024-12-17 | 45643.875 | 580.7363 | 0.67157 | 142.7565 | 9.0873 | 125.9525 | 22.6334 | 22.4869 | 9.927 | 1980.3798 | 3.2539 | 3.4292 | 138.3271 | 134.0767 | 117.3357 | 142.2271 | 153.4448 | 151.322 | 1194.9381 | 1396.6312 | 1185.0525 | 795.3365 | 8.7896
2024-12-17 | 45643.9167 | 553.7025 | 0.68246 | 148.3466 | 14.7763 | 111.1619 | 18.9167 | 26.6046 | 19.4242 | 1868.5714 | 3.3619 | 3.3377 | 135.1497 | 131.3234 | 114.9945 | 139.11 | 151.4881 | 149.1473 | 1069.8096 | 1241.6002 | 1087.9015 | 780.7072 | 6.731
2024-12-17 | 45643.9583 | 461.4253 | 0.64886 | 119.314 | 7.7073 | 90.5346 | 12.5876 | 11.2856 | 5.3353 | 1626.1797 | 3.9334 | 3.9194 | 132.008 | 129.4347 | 113.8658 | 134.7207 | 146.7548 | 144.517 | 861.0396 | 991.6084 | 915.1364 | 711.0234 | 6.5886
2024-12-17 | 45644 | 326.0827 | 0.70521 | 81.1815 | 8.1096 | 67.1149 | 14.0821 | 8.7701 | 0 | 1372.1001 | 4.6303 | 4.4926 | 121.4057 | 119.6838 | 106.557 | 122.098 | 133.0993 | 130.8569 | 619.4503 | 697.8424 | 786.2222 | 585.8813 | 0.78068
2024-12-18 | 45644.0417 | 339.93 | 0.72033 | 83.1831 | 11.7931 | 68.1675 | 20.1177 | 8.9137 | 2.7158 | 1391.2711 | 4.6338 | 4.2251 | 120.7048 | 117.8811 | 105.6549 | 118.6787 | 129.9615 | 127.3719 | 644.2668 | 710.3674 | 798.8234 | 592.4556 | 0.18464
2024-12-18 | 45644.0833 | 361.093 | 0.69698 | 87.5838 | 9.5269 | 77.652 | 21.7023 | 6.3336 | 4.692 | 1422.1116 | 4.5671 | 4.1615 | 124.7097 | 121.6541 | 108.9698 | 119.7062 | 131.208 | 128.4021 | 685.9596 | 749.6375 | 817.0583 | 605.0491 | -0.069846
2024-12-18 | 45644.125 | 334.3385 | 0.70879 | 80.1944 | 10.6287 | 71.6057 | 23.7756 | 6.1652 | 0 | 1380.2528 | 4.7176 | 4.2278 | 122.3772 | 119.7125 | 107.501 | 118.2255 | 129.505 | 126.6705 | 636.7203 | 695.6883 | 786.3964 | 593.8222 | 0.37035
2024-12-18 | 45644.1667 | 333.4605 | 0.6822 | 86.4176 | 7.1294 | 65.4551 | 8.7833 | 6.0353 | 1.4304 | 1378.8453 | 4.8431 | 4.3276 | 121.4565 | 118.8109 | 107.0495 | 116.9245 | 128.3444 | 125.5103 | 637.9375 | 693.7953 | 785.723 | 593.1209 | 0.91458
2024-12-18 | 45644.2083 | 335.3864 | 0.69543 | 86.5645 | 10.5202 | 64.1832 | 10.9756 | 4.0898 | 0.79924 | 1399.4678 | 4.7757 | 4.2493 | 120.7789 | 117.8501 | 106.1148 | 115.5704 | 127.0704 | 124.2896 | 646.5692 | 694.9417 | 794.6144 | 604.849 | 0.91364
2024-12-18 | 45644.25 | 480.5741 | 0.68544 | 119.3938 | 11.7384 | 114.707 | 21.5539 | 14.9535 | 8.5064 | 1846.0292 | 4.0157 | 3.848 | 131.4334 | 126.718 | 112.1289 | 124.4208 | 136.9713 | 133.4868 | 1049.2125 | 1131.894 | 1086.0334 | 759.9998 | 0.86024
2024-12-18 | 45644.2917 | 576.6313 | 0.64698 | 131.9179 | 6.8513 | 121.898 | 8.1011 | 11.5229 | 3.3351 | 2023.5101 | 3.3382 | 3.6652 | 135.7728 | 131.3963 | 115.1441 | 136.4807 | 149.5707 | 145.9533 | 1221.4803 | 1398.8275 | 1193.5667 | 829.944 | 6.9841
2024-12-18 | 45644.3333 | 576.9386 | 0.64214 | 133.7138 | 13.3565 | 116.6676 | 23.8356 | 17.6065 | 7.1951 | 1951.8768 | 2.8198 | 3.3354 | 134.9523 | 131.1356 | 114.9061 | 138.1195 | 150.1083 | 147.4314 | 1155.478 | 1332.8502 | 1143.9652 | 807.9331 | 4.9791
2024-12-18 | 45644.375 | 580.4733 | 0.62779 | 139.64 | 13.5729 | 113.6323 | 15.8737 | 22.9267 | 9.0743 | 1962.5818 | 2.8158 | 3.3724 | 134.5703 | 130.458 | 114.4867 | 137.2121 | 150.3504 | 146.9024 | 1150.327 | 1337.078 | 1158.254 | 804.3281 | 6.5697
2024-12-18 | 45644.4167 | 578.7622 | 0.62899 | 138.4267 | 13.3967 | 118.5582 | 18.3727 | 25.3295 | 10.2073 | 1966.8038 | 2.7162 | 3.3898 | 135.7632 | 131.5844 | 115.5364 | 138.9538 | 151.8375 | 148.6783 | 1154.4758 | 1347.0056 | 1168.3053 | 798.5264 | 7.2272
2024-12-18 | 45644.4583 | 566.3233 | 0.62206 | 130.0068 | 12.9461 | 118.5515 | 21.7442 | 23.8009 | 9.2313 | 1924.4834 | 2.8121 | 3.4328 | 136.6862 | 132.697 | 116.8255 | 140.9717 | 153.4445 | 150.5757 | 1120.1672 | 1323.5398 | 1149.0061 | 775.5291 | 8.5375
2024-12-18 | 45644.5 | 433.5514 | 0.6306 | 101.2195 | 5.1122 | 80.2163 | 16.7489 | 13.9689 | 0.52812 | 1537.0995 | 3.7273 | 3.8266 | 131.0748 | 128.7639 | 114.7675 | 134.7665 | 146.0599 | 144.3249 | 778.9612 | 913.2855 | 910.053 | 627.0607 | 1.3026
2024-12-18 | 45644.5417 | 387.2363 | 0.65075 | 89.2078 | 4.1379 | 69.0723 | 17.4224 | 19.5122 | 0 | 1432.3816 | 3.5058 | 3.8575 | 126.8218 | 124.7634 | 111.867 | 128.1406 | 138.6361 | 137.2667 | 679.472 | 781.1686 | 842.1616 | 590.2395 | 1.0175
2024-12-18 | 45644.5833 | 370.4416 | 0.65573 | 81.3513 | 4.5293 | 62.9511 | 16.2901 | 18.3136 | 0 | 1413.8101 | 3.6762 | 4.0264 | 130.4755 | 128.4987 | 115.1935 | 123.5371 | 133.8423 | 132.3035 | 713.1704 | 709.2079 | 830.5618 | 583.2785 | 46.55
2024-12-18 | 45644.625 | 288.0481 | 0.66592 | 57.0678 | 0.42881 | 47.5523 | 9.4222 | 0 | 0 | 1276.1381 | 4.6405 | 4.6973 | 132.203 | 131.4463 | 118.806 | 112.7491 | 122.5648 | 120.7791 | 625.4216 | 550.2986 | 772.3696 | 503.7783 | 76.0099
2024-12-18 | 45644.6667 | 294.8871 | 0.6789 | 60.4134 | 0 | 52.6578 | 11.9589 | 4.5457 | 0 | 1279.7683 | 4.4876 | 4.5948 | 131.3361 | 130.3033 | 117.8661 | 110.8541 | 120.6239 | 118.5022 | 624.2427 | 548.178 | 768.1689 | 511.5922 | 59.7588
2024-12-18 | 45644.7083 | 300.897 | 0.68726 | 63.8433 | 0 | 55.5892 | 13.8741 | 11.68 | 0 | 1293.3175 | 4.4765 | 4.5675 | 132.988 | 131.913 | 119.3564 | 112.8288 | 122.6543 | 120.6393 | 641.47 | 567.9778 | 769.4338 | 523.8546 | 63.1424
2024-12-18 | 45644.75 | 308.0986 | 0.69333 | 69.5476 | 0.47214 | 60.6255 | 15.622 | 12.9138 | 0 | 1318.1367 | 4.5237 | 4.5454 | 133.4297 | 131.537 | 120.0772 | 113.6715 | 123.2842 | 121.3742 | 666.3516 | 589.7183 | 772.3578 | 545.7832 | 67.9129
2024-12-18 | 45644.7917
2024-12-18 | 45644.8333
2024-12-18 | 45644.875
2024-12-18 | 45644.9167
2024-12-18 | 45644.9583
2024-12-18 | 45645
2024-12-22 | 45645.0417 | 329.2722 | 0.66052 | 69.9118 | 0 | 54.9678 | 6.0412 | 0 | 0 | 1390.4569 | 3.9406 | 4.8073 | 116.3075 | 116.1439 | 102.0379 | 115.3189 | 125.9032 | 125.8693 | 667.5779 | 707.6406 | 813.7578 | 576.7016 | -0.097656
2024-12-22 | 45645.0833 | 327.8986 | 0.65602 | 65.529 | 0 | 52.2087 | 5.5247 | 0 | 0 | 1391.5607 | 4.0051 | 4.9565 | 114.6877 | 114.4408 | 100.4069 | 114.2778 | 125.6119 | 125.6233 | 663.3867 | 705.6358 | 815.6074 | 575.957 | -0.097656
2024-12-22 | 45645.125 | 326.4129 | 0.65889 | 65.0705 | 0 | 51.5457 | 4.7325 | 0 | 0 | 1391.3784 | 3.9777 | 5.0237 | 114.3187 | 114.0737 | 100.0347 | 113.5294 | 124.9346 | 125.1405 | 662.4023 | 700.9409 | 816.1658 | 575.2001 | -0.097656
2024-12-22 | 45645.1667 | 328.8007 | 0.65146 | 64.4112 | 0 | 50.6046 | 1.0132 | 0 | 0 | 1392.4949 | 3.9488 | 5.0268 | 114.4352 | 114.2844 | 100.007 | 113.4928 | 125.0737 | 125.1603 | 669.2978 | 707.5259 | 817.7917 | 574.6844 | -0.097656
2024-12-22 | 45645.2083 | 329.2628 | 0.64624 | 64.2983 | 0 | 50.6194 | 2.5303 | 0 | 0 | 1392.8373 | 3.9958 | 5.0262 | 115.1147 | 114.8897 | 100.4933 | 113.8058 | 125.2561 | 125.5782 | 678.0005 | 714.8443 | 818.1843 | 574.6415 | 0.027886
2024-12-22 | 45645.25 | 334.1194 | 0.63464 | 63.5819 | 0.34002 | 49.4774 | 0.66365 | 0 | 0 | 1394.363 | 3.9361 | 4.954 | 115.4263 | 115.2269 | 100.7563 | 114.0014 | 125.7089 | 126.0951 | 681.9933 | 718.0757 | 818.5189 | 575.8602 | -0.097656
2024-12-22 | 45645.2917 | 355.6815 | 0.6366 | 70.4052 | 4.7893 | 56.6131 | 3.0861 | 9.2077 | 2.4273 | 1431.6754 | 3.7799 | 4.6249 | 116.9072 | 116.373 | 101.5125 | 114.6757 | 126.7613 | 126.9412 | 717.397 | 749.6423 | 823.7459 | 607.9225 | -0.097656
2024-12-22 | 45645.3333 | 520.4005 | 0.63166 | 124.6553 | 7.5071 | 99.2078 | 21.2942 | 28.0009 | 10.9809 | 1846.8134 | 3.5101 | 3.6372 | 132.2572 | 128.949 | 112.2855 | 124.7949 | 138.5789 | 137.9218 | 1140.6304 | 1188.0397 | 1081.6066 | 765.2163 | 4.7346
2024-12-22 | 45645.375 | 583.1588 | 0.61703 | 136.1989 | 19.1293 | 99.9746 | 22.9223 | 34.3045 | 21.7755 | 1976.8489 | 3.2973 | 3.922 | 132.6126 | 129.5049 | 112.1267 | 132.4226 | 147.0951 | 146.6874 | 1235.2341 | 1382.4982 | 1181.1288 | 795.7244 | 12.9457
2024-12-22 | 45645.4167 | 583.9515 | 0.61788 | 141.9389 | 21.7514 | 116.0991 | 28.3216 | 38.646 | 24.1289 | 1903.2344 | 2.8745 | 3.612 | 132.537 | 129.5914 | 112.7216 | 134.1326 | 147.8713 | 147.9619 | 1162.2557 | 1303.5664 | 1128.8601 | 774.3644 | 9.5804
2024-12-22 | 45645.4583 | 592.0027 | 0.60577 | 147.6689 | 20.1646 | 120.4263 | 18.4772 | 35.3756 | 24.7887 | 1956.0558 | 2.4324 | 3.6805 | 132.5553 | 129.5157 | 112.9878 | 135.2032 | 148.7767 | 148.9295 | 1193.6273 | 1357.7164 | 1193.6173 | 762.41 | 8.6474
2024-12-22 | 45645.5 | 588.2883 | 0.59936 | 138.1869 | 17.1643 | 115.9134 | 17.0706 | 37.8223 | 25.2774 | 1983.2529 | 2.935 | 3.769 | 132.5153 | 129.2894 | 113.0077 | 137.3228 | 150.8546 | 151.2587 | 1206.6693 | 1402.9819 | 1214.9784 | 768.3004 | 12.3549
2024-12-22 | 45645.5417 | 586.3881 | 0.60818 | 141.7449 | 18.7576 | 110.7443 | 15.2527 | 36.4234 | 22.4516 | 1951.7211 | 2.9021 | 3.6597 | 134.8737 | 131.927 | 114.9958 | 139.7392 | 152.2111 | 153.0224 | 1187.6824 | 1373.2863 | 1189.8636 | 761.8348 | 11.1852
2024-12-22 | 45645.5833 | 575.0966 | 0.60463 | 131.4156 | 22.0849 | 107.6875 | 16.8466 | 33.7342 | 24.7579 | 1895.4919 | 2.8352 | 3.6263 | 133.5529 | 130.7575 | 114.1018 | 139.6687 | 152.649 | 153.2464 | 1113.8414 | 1307.9221 | 1141.7885 | 753.7383 | 11.0997
2024-12-22 | 45645.625 | 480.2846 | 0.58943 | 105.3968 | 13.416 | 89.4223 | 15.8463 | 24.7618 | 7.5317 | 1679.3904 | 3.7407 | 4.013 | 130.0539 | 128.1674 | 112.3135 | 135.7799 | 148.2026 | 148.6104 | 921.4075 | 1068.621 | 1038.4041 | 641.0052 | 8.7937
2024-12-22 | 45645.6667 | 331.5672 | 0.63374 | 66.7207 | 3.8947 | 57.128 | 15.2807 | 1.9649 | 0 | 1315.1324 | 4.7914 | 4.6001 | 120.9765 | 120.0064 | 106.8455 | 123.4777 | 134.5977 | 134.9458 | 635.6143 | 713.2228 | 871.6287 | 443.4477 | 3.1353
2024-12-22 | 45645.7083 | 317.4816 | 0.64632 | 64.7125 | 4.3834 | 56.4521 | 11.8333 | 7.8755 | 0.8814 | 1305.8595 | 4.6825 | 4.705 | 119.1275 | 117.6071 | 105.5142 | 119.3016 | 130.2906 | 130.552 | 620.2286 | 682.2462 | 846.8581 | 458.9802 | 0.83671
2024-12-22 | 45645.75 | 424.8311 | 0.62808 | 98.9112 | 5.188 | 95.7764 | 10.6716 | 31.5901 | 1.5752 | 1675.1873 | 4.4032 | 3.8887 | 127.4887 | 124.6358 | 110.1561 | 122.6745 | 134.8206 | 134.7112 | 914.025 | 984.5421 | 1006.4631 | 668.7255 | 2.4649
2024-12-22 | 45645.7917 | 562.778 | 0.6138 | 115.5204 | 16.0015 | 100.6045 | 21.9207 | 30.262 | 0 | 2028.9801 | 3.7645 | 3.8873 | 134.3584 | 131.0489 | 113.9095 | 134.2677 | 148.1611 | 148.1306 | 1239.0386 | 1410.2096 | 1214.9836 | 813.9978 | 11.0704
2024-12-22 | 45645.8333 | 568.5408 | 0.61197 | 91.77 | 13.3979 | 68.3054 | 23.5168 | 23.7862 | 0 | 1949.7112 | 3.5448 | 3.8871 | 130.9521 | 128.1613 | 111.0247 | 135.3498 | 149.0527 | 149.1344 | 1141.5822 | 1338.1957 | 1161.8077 | 787.9146 | 12.7838
2024-12-22 | 45645.875 | 538.8615 | 0.58225 | 90.173 | 9.2515 | 74.0733 | 17.6077 | 13.3151 | 0 | 1892.5398 | 3.9363 | 4.1658 | 129.7317 | 127.4321 | 110.651 | 133.71 | 146.4362 | 146.6431 | 1091.4856 | 1260.1569 | 1183.3209 | 709.1694 | 10.4092
2024-12-22 | 45645.9167 | 411.9991 | 0.58399 | 57.0956 | 5.7378 | 58.9441 | 17.7001 | 21.4576 | 0.028831 | 1664.1476 | 4.9939 | 4.6441 | 120.711 | 118.3799 | 103.8774 | 122.4094 | 134.6002 | 134.1684 | 873.3411 | 989.0804 | 1128.3358 | 535.8069 | 5.8517
2024-12-22 | 45645.9583 | 334.6933 | 0.60019 | 47.8303 | 6.1366 | 41.5958 | 7.4858 | 5.0843 | 0.056795 | 1372.5177 | 4.8387 | 4.8731 | 116.5792 | 114.9143 | 101.8587 | 115.7691 | 127.1495 | 126.5381 | 660.5894 | 732.045 | 916.6523 | 455.8658 | 1.1635
2024-12-22 | 45646 | 322.2395 | 0.61445 | 53.9286 | 0.63395 | 48.8585 | 9.9511 | 6.5711 | 0.039849 | 1294.0493 | 4.4415 | 4.6171 | 116.7083 | 116.1717 | 102.7862 | 112.865 | 124.0903 | 123.994 | 608.1463 | 663.104 | 827.7689 | 466.2833 | 0.37109
2024-12-23 | 45646.0417 | 455.6123 | 0.63139 | 99.2335 | 13.1441 | 90.0073 | 24.8035 | 32.3221 | 3.7857 | 1674.8439 | 3.713 | 3.6348 | 126.6244 | 124.1708 | 108.7073 | 118.728 | 131.1506 | 130.7652 | 927.2269 | 981.7711 | 1003.393 | 671.5011 | 0.49169
2024-12-23 | 45646.0833 | 413.4854 | 0.6148 | 75.2582 | 6.7192 | 86.6007 | 23.3762 | 27.752 | 0 | 1525.5496 | 4.5233 | 3.7907 | 125.8965 | 124.4397 | 109.2381 | 119.6362 | 132.0138 | 131.604 | 795.4933 | 859.7357 | 947.8143 | 577.7675 | 0.856
2024-12-23 | 45646.125 | 415.725 | 0.64956 | 82.973 | 6.2648 | 97.7054 | 22.7368 | 49.6776 | 0 | 1545.8678 | 4.1274 | 3.4376 | 124.3638 | 122.2005 | 107.9459 | 117.6247 | 129.8492 | 129.402 | 804.0041 | 859.5388 | 966.6578 | 579.2142 | 0
2024-12-23 | 45646.1667 | 402.1281 | 0.62964 | 46.05 | 4.752 | 63.3175 | 19.8576 | 34.3823 | 0 | 1536.4103 | 4.5578 | 3.9602 | 121.9075 | 120.3144 | 105.4371 | 118.3479 | 130.7574 | 130.6707 | 801.3091 | 850.1253 | 982.4426 | 553.9743 | 0.49643
2024-12-23 | 45646.2083 | 404.4566 | 0.66302 | 77.77 | 9.034 | 74.9291 | 14.2166 | 27.9319 | 5.5489 | 1543.6628 | 4.1051 | 4.038 | 121.9602 | 120.5674 | 105.4399 | 119.6805 | 130.3186 | 130.7551 | 811.8618 | 859.2228 | 893.7299 | 649.9151 | 0.54867
2024-12-23 | 45646.25 | 545.1461 | 0.64277 | 111.2134 | 13.9363 | 90.5874 | 17.6038 | 27.8892 | 12.367 | 1928.3645 | 3.5831 | 4.1043 | 132.0563 | 129.6085 | 112.1448 | 130.8356 | 144.4966 | 144.5653 | 1162.7728 | 1285.2766 | 1107.7351 | 820.6292 | 9.9363
2024-12-23 | 45646.2917 | 576.1572 | 0.64262 | 123.0355 | 17.475 | 101.9592 | 21.7814 | 38.1591 | 20.419 | 1948.8617 | 3.399 | 3.929 | 132.3864 | 129.901 | 111.9288 | 134.4153 | 148.5866 | 148.9905 | 1182.7144 | 1352.3221 | 1145.6023 | 803.2369 | 15.2636
2024-12-23 | 45646.3333 | 579.4087 | 0.64066 | 123.6899 | 19.6717 | 104.3344 | 24.429 | 33.3374 | 19.8367 | 1915.8237 | 3.1921 | 3.6659 | 132.8596 | 130.6905 | 112.4512 | 136.2842 | 149.9219 | 151.0621 | 1144.9221 | 1321.689 | 1113.6376 | 802.1706 | 14.6353
2024-12-23 | 45646.375 | 584.9573 | 0.62578 | 131.4276 | 16.4336 | 111.9403 | 27.6875 | 35.5133 | 17.1183 | 1918.7188 | 3.1112 | 3.3842 | 134.7835 | 132.4324 | 113.9842 | 137.0184 | 150.6804 | 151.8221 | 1167.3557 | 1335.2472 | 1105.3545 | 813.3597 | 12.9798
2024-12-23 | 45646.4167 | 566.0118 | 0.6302 | 135.9937 | 21.023 | 115.0214 | 29.8775 | 32.2875 | 25.6297 | 1885.808 | 2.7785 | 3.417 | 134.7995 | 133.2688 | 114.6908 | 140.0364 | 153.4387 | 154.8533 | 1084.5757 | 1261.2817 | 961.5695 | 924.2164 | 14.1774
2024-12-23 | 45646.4583 | 585.5793 | 0.62433 | 137.9288 | 18.5503 | 122.8115 | 18.1868 | 37.1494 | 26.4751 | 1965.6077 | 3.0917 | 3.3201 | 136.1991 | 134.1876 | 115.6011 | 140.4548 | 154.2845 | 155.3356 | 1172.5508 | 1356.014 | 1045.1813 | 920.4413 | 19.3197
2024-12-23 | 45646.5 | 588.5551 | 0.60829 | 131.3834 | 22.6331 | 121.5365 | 21.6872 | 39.4447 | 28.454 | 1975.5342 | 2.9538 | 3.7138 | 133.9934 | 131.8151 | 113.8655 | 142.7395 | 156.371 | 157.327 | 1162.4602 | 1401.713 | 1170.5442 | 805.0009 | 12.8268
2024-12-23 | 45646.5417 | 581.1846 | 0.60383 | 131.4527 | 27.4697 | 118.7642 | 24.6594 | 33.1708 | 28.5462 | 1954.4254 | 2.4215 | 3.729 | 131.7105 | 129.2291 | 111.7261 | 141.2762 | 154.7038 | 155.303 | 1128.8672 | 1360.9535 | 1181.5067 | 772.8954 | 10.1644
2024-12-23 | 45646.5833 | 466.9659 | 0.5912 | 99.0736 | 12.8553 | 83.2242 | 16.8507 | 7.6174 | 3.8343 | 1580.9589 | 3.5045 | 4.3146 | 127.5067 | 126.5963 | 110.3581 | 136.4034 | 148.5031 | 149.4181 | 829.9811 | 986.6171 | 936.7434 | 644.1445 | 6.9312
2024-12-23 | 45646.625 | 553.301 | 0.60976 | 121.7378 | 17.0207 | 97.3898 | 17.037 | 32.3065 | 19.2456 | 1974.8698 | 3.6343 | 3.9476 | 133.3841 | 130.9035 | 113.5849 | 137.8718 | 150.0992 | 150.5754 | 1179.3553 | 1373.287 | 1188.9709 | 785.8973 | 9.4396
2024-12-23 | 45646.6667 | 582.3315 | 0.59527 | 108.1724 | 21.2286 | 91.0952 | 18.1231 | 30.8692 | 22.1464 | 2014.798 | 3.6928 | 4.2168 | 131.7785 | 129.2177 | 112.1241 | 142.3537 | 155.6562 | 155.9919 | 1182.9065 | 1460.7672 | 1224.4537 | 790.3659 | 17.9312
2024-12-23 | 45646.7083 | 583.6434 | 0.59214 | 113.0054 | 21.7323 | 95.5441 | 23.3436 | 30.3942 | 21.694 | 1994.2886 | 3.6405 | 3.9986 | 131.4541 | 128.6398 | 111.6205 | 142.6077 | 155.9795 | 156.258 | 1161.5135 | 1428.2646 | 1213.343 | 780.9278 | 15.4966
2024-12-23 | 45646.75 | 585.3503 | 0.584 | 109.106 | 13.3871 | 100.7286 | 26.0789 | 34.2871 | 12.7352 | 2000.8114 | 3.6987 | 3.8031 | 131.4575 | 128.4817 | 111.3573 | 140.5167 | 153.8992 | 154.1397 | 1172.1323 | 1411.446 | 1239.7136 | 761.0786 | 15.0436
2024-12-23 | 45646.7917 | 581.5672 | 0.57886 | 102.2517 | 12.11 | 95.8227 | 13.0889 | 29.4527 | 4.4335 | 1991.0509 | 3.5009 | 3.9465 | 131.1246 | 128.1172 | 111.0557 | 141.0374 | 154.284 | 154.4128 | 1163.3435 | 1412.3198 | 1233.2084 | 757.8358 | 12.6611
2024-12-23 | 45646.8333 | 574.6857 | 0.58054 | 90.3428 | 7.497 | 81.463 | 22.277 | 25.5895 | 0 | 1978.8524 | 3.7268 | 3.6948 | 131.265 | 128.5037 | 111.2763 | 139.9815 | 152.5738 | 152.6376 | 1157.718 | 1378.7836 | 1229.8907 | 748.9533 | 11.6963
2024-12-23 | 45646.875 | 564.3557 | 0.56635 | 98.7975 | 7.4813 | 89.9798 | 19.9277 | 39.4061 | 0.45329 | 1971.0946 | 4.1067 | 3.9382 | 130.3233 | 127.3708 | 110.3842 | 136.4227 | 149.6814 | 149.5453 | 1157.7101 | 1369.6937 | 1260.0658 | 711.0396 | 13.0161
2024-12-23 | 45646.9167 | 495.7552 | 0.56972 | 84.9277 | 12.8405 | 61.4461 | 17.4937 | 25.6001 | 4.2551 | 1837.1156 | 4.6758 | 4.8925 | 125.2697 | 123.0526 | 106.6761 | 135.528 | 148.5485 | 148.4875 | 1025.5334 | 1256.7343 | 1175.2988 | 661.7781 | 14.9072
2024-12-23 | 45646.9583 | 360.5662 | 0.59077 | 60.1465 | 8.4634 | 34.5086 | 4.2694 | 0 | 0 | 1491.4917 | 5.4303 | 5.2742 | 116.6785 | 114.8641 | 101.2544 | 125.0986 | 136.521 | 136.3481 | 744.4518 | 865.0535 | 1023.4196 | 468.0567 | 4.7754
2024-12-23 | 45647 | 382.5718 | 0.58687 | 65.1696 | 8.5389 | 49.5018 | 6.8679 | 10.4672 | 6.5913 | 1467.203 | 4.7054 | 4.8048 | 119.7973 | 118.3738 | 104.2025 | 123.3151 | 134.7181 | 134.6677 | 736.5847 | 820.7065 | 926.2343 | 540.9772 | 1.51
2024-12-24 | 45647.0417 | 322.132 | 0.62096 | 60.1827 | 1.797 | 46.2513 | 0.65149 | 1.3277 | 0.56861 | 1286.1246 | 4.4629 | 4.8342 | 115.831 | 115.4538 | 101.982 | 119.2647 | 130.0244 | 130.5073 | 603.1757 | 660.9475 | 807.8127 | 478.3224 | 0.19577
2024-12-24 | 45647.0833 | 324.3805 | 0.62227 | 61.3231 | 1.9744 | 50.8646 | 0.97123 | 0 | 0 | 1292.5697 | 4.4804 | 4.765 | 117.3215 | 117.1304 | 103.5088 | 118.7536 | 129.5533 | 130.1092 | 617.1176 | 668.92 | 813.8231 | 478.7476 | 0.17578
2024-12-24 | 45647.125 | 325.4212 | 0.62278 | 65.0653 | 2.9216 | 55.6504 | 2.0869 | 0 | 0 | 1293.7196 | 4.4231 | 4.7311 | 117.2141 | 117.0917 | 103.3574 | 118.515 | 129.3461 | 129.9514 | 615.5137 | 669.3345 | 813.5507 | 480.1898 | 0.17578
2024-12-24 | 45647.1667 | 324.4778 | 0.62259 | 63.182 | 1.2371 | 57.4649 | 5.1847 | 0 | 0 | 1291.6248 | 4.4555 | 4.8226 | 116.8843 | 116.8382 | 102.941 | 118.524 | 129.5956 | 130.1395 | 617.6724 | 669.7687 | 809.2568 | 482.3656 | 0.17578
2024-12-24 | 45647.2083 | 324.2881 | 0.62906 | 61.9009 | 0.11708 | 59.0775 | 4.3448 | 2.6684 | 0 | 1294.2307 | 4.5917 | 4.7517 | 116.1075 | 116.1441 | 102.1536 | 117.4677 | 128.6969 | 129.0876 | 613.1904 | 663.0916 | 813.2041 | 481.0395 | 0.17578
2024-12-24 | 45647.25 | 350.3922 | 0.64227 | 71.902 | 6.9399 | 64.0687 | 6.2354 | 19.154 | 8.2243 | 1398.5001 | 4.6919 | 4.6259 | 116.6997 | 115.9715 | 101.6849 | 116.7711 | 128.5698 | 128.7167 | 690.6848 | 740.7136 | 858.4885 | 540.0048 | 0.17578
2024-12-24 | 45647.2917 | 540.936 | 0.62304 | 143.5583 | 15.0666 | 124.3386 | 17.0645 | 32.8123 | 12.3997 | 1854.3398 | 3.412 | 3.6215 | 131.2434 | 128.3468 | 110.95 | 129.2715 | 142.5916 | 142.2813 | 1119.6702 | 1209.9615 | 1056.9135 | 797.4222 | 1.2148
2024-12-24 | 45647.3333 | 580.2678 | 0.59478 | 113.231 | 15.9536 | 98.4797 | 22.0034 | 33.8808 | 9.1835 | 1906.0682 | 2.9589 | 3.6818 | 131.6922 | 129.5556 | 110.9947 | 135.2041 | 148.433 | 148.2936 | 1148.4301 | 1295.2792 | 1105.5247 | 800.5731 | 2.6358
2024-12-24 | 45647.375 | 584.9625 | 0.59022 | 124.6801 | 17.1344 | 111.2345 | 20.7648 | 34.9062 | 15.1285 | 1908.6816 | 2.7476 | 3.8122 | 131.8978 | 129.6618 | 111.3791 | 136.5508 | 149.7974 | 149.9056 | 1155.72 | 1313.8859 | 1127.8739 | 780.8657 | 5.0776
2024-12-24 | 45647.4167 | 581.2429 | 0.59417 | 129.4827 | 19.5635 | 118.3366 | 22.0369 | 31.7906 | 16.2763 | 1902.0868 | 2.5806 | 3.7015 | 131.9127 | 129.2742 | 111.4325 | 137.3137 | 150.8796 | 151.1156 | 1136.7094 | 1310.7408 | 1129.2312 | 772.8325 | 7.9532
2024-12-24 | 45647.4583 | 583.2607 | 0.59919 | 134.2204 | 15.6225 | 125.7396 | 19.34 | 30.84 | 11.5532 | 1905.6664 | 2.6093 | 3.7239 | 132.5981 | 129.9954 | 112.1801 | 139.296 | 152.6021 | 153.036 | 1137.1543 | 1322.0824 | 1135.787 | 769.8516 | 8.4736
2024-12-24 | 45647.5 | 568.3222 | 0.58897 | 124.021 | 15.1865 | 110.1224 | 21.0161 | 35.533 | 9.8476 | 1854.6016 | 3.232 | 3.7407 | 132.5175 | 130.1448 | 112.7042 | 140.3878 | 153.5632 | 154.044 | 1088.1401 | 1285.6389 | 1124.6183 | 729.9772 | 10.1976
2024-12-24 | 45647.5417 | 495.0633 | 0.57676 | 108.4681 | 17.1748 | 79.0742 | 19.7948 | 22.0487 | 6.2497 | 1671.2378 | 3.7226 | 4.2391 | 129.2751 | 127.686 | 111.2414 | 137.69 | 150.1554 | 150.8137 | 924.5253 | 1081.0773 | 1013.842 | 657.4102 | 8.4911
2024-12-24 | 45647.5833 | 411.5038 | 0.61773 | 96.9601 | 11.9439 | 73.786 | 11.5256 | 15.5905 | 5.9317 | 1499.7848 | 3.9928 | 4.3963 | 123.7755 | 122.3642 | 107.9713 | 129.9746 | 141.3409 | 142.0632 | 751.0296 | 849.201 | 875.7965 | 624.0386 | 2.5817
2024-12-24 | 45647.625 | 550.3214 | 0.59695 | 124.2582 | 17.1157 | 106.2645 | 27.6245 | 29.7444 | 4.9343 | 1785.2639 | 3.3113 | 3.2555 | 133.5959 | 131.0537 | 114.5421 | 134.8939 | 147.4013 | 147.8341 | 1042.6633 | 1153.0978 | 1073.079 | 712.1824 | 3.3309
2024-12-24 | 45647.6667 | 566.709 | 0.60364 | 138.8499 | 20.1142 | 112.3805 | 25.0795 | 27.8511 | 15.6745 | 1853.9417 | 2.5759 | 3.6941 | 134.214 | 132.0632 | 114.8904 | 139.7004 | 152.8132 | 153.5078 | 1076.7059 | 1248.3713 | 1067.3051 | 786.6443 | 4.9386
2024-12-24 | 45647.7083
2024-12-24 | 45647.75
2024-12-24 | 45647.7917
2024-12-24 | 45647.8333
2024-12-24 | 45647.875
2024-12-24 | 45647.9167 | 464.0503 | 0.57332 | 92.0409 | 5.0151 | 84.6479 | 8.4247 | 8.6815 | 0.28142 | 1869.8859 | 5.1913 | 5.0178 | 127.211 | 125.14 | 109.1311 | 129.0509 | 142.043 | 141.4297 | 1052.6091 | 1215.855 | 1193.7863 | 676.0782 | 8.5657
2024-12-24 | 45647.9583 | 335.405 | 0.60912 | 61.542 | 1.3236 | 56.7596 | 5.1849 | 0 | 0 | 1425.2863 | 5.339 | 5.0519 | 118.0775 | 116.9755 | 103.5251 | 118.5973 | 129.951 | 129.8588 | 669.3267 | 740.3842 | 854.3509 | 570.9249 | 0.69182
2024-12-24 | 45648 | 478.8812 | 0.61434 | 109.7107 | 8.1495 | 91.408 | 7.834 | 21.4676 | 6.4991 | 1783.8098 | 4.6085 | 4.0424 | 127.1979 | 124.1849 | 108.8467 | 123.1758 | 136.0184 | 135.5473 | 989.5806 | 1079.8243 | 1013.7034 | 770.1499 | 1.3743
2024-12-25 | 45648.0417 | 451.0188 | 0.59152 | 97.1899 | 5.5643 | 77.652 | 5.3096 | 11.2045 | 4.5918 | 1733.3376 | 5.108 | 4.5949 | 127.6866 | 125.6358 | 109.7288 | 128.2807 | 141.4335 | 141.209 | 944.8198 | 1067.8839 | 1005.4044 | 727.9261 | 6.025
2024-12-25 | 45648.0833 | 335.7462 | 0.61521 | 62.1761 | 3.7497 | 49.4387 | 0 | 0 | 0 | 1440.3861 | 5.2085 | 5.0345 | 118.7107 | 117.7351 | 103.8024 | 119.025 | 130.6641 | 130.566 | 681.9064 | 757.1103 | 863.3005 | 577.0774 | 0.79809
2024-12-25 | 45648.125 | 336.864 | 0.62365 | 65.5025 | 4.1432 | 45.4753 | 0.17281 | 0 | 0 | 1436.4125 | 5.1717 | 4.9021 | 119.1463 | 118.0541 | 104.305 | 116.6549 | 128.3629 | 128.4654 | 687.7747 | 754.0507 | 861.8235 | 574.5871 | 0.33203
2024-12-25 | 45648.1667 | 339.018 | 0.6147 | 65.8447 | 4.6344 | 47.3948 | 0 | 0 | 0 | 1445.1263 | 5.1676 | 4.8902 | 118.3629 | 117.1894 | 103.3578 | 115.9042 | 127.836 | 127.8367 | 695.2425 | 761.8375 | 872.0784 | 573.0861 | 0.33203
2024-12-25 | 45648.2083 | 334.982 | 0.62619 | 65.0642 | 3.7175 | 46.9594 | 0 | 0 | 0 | 1436.0906 | 5.2303 | 4.8987 | 118.3603 | 117.1603 | 103.3216 | 115.5955 | 127.5244 | 127.3739 | 690.8181 | 751.4173 | 863.143 | 572.9529 | 0.33203
2024-12-25 | 45648.25 | 333.8968 | 0.62625 | 62.2122 | 4.0459 | 45.3364 | 0 | 0 | 0 | 1435.035 | 5.182 | 4.8256 | 118.1559 | 117.1525 | 103.3023 | 115.1849 | 127.2567 | 127.1502 | 683.9021 | 742.9969 | 862.6909 | 572.3492 | 0.33203
2024-12-25 | 45648.2917 | 398.5639 | 0.64683 | 75.0303 | 5.195 | 60.7543 | 8.6229 | 15.1693 | 6.7178 | 1597.0054 | 4.9022 | 4.2523 | 122.599 | 120.3266 | 106.2351 | 118.1998 | 130.4439 | 130.3042 | 813.0638 | 872.8973 | 920.2067 | 676.8059 | 0.52782
2024-12-25 | 45648.3333 | 538.4371 | 0.62189 | 103.291 | 8.3628 | 91.0564 | 15.7303 | 27.6262 | 1.8582 | 1860.9489 | 4.0034 | 3.4675 | 131.4891 | 127.8812 | 111.7079 | 126.1617 | 139.9888 | 139.4058 | 1090.1604 | 1186.0522 | 1093.7245 | 767.23 | 0.78069
2024-12-25 | 45648.375 | 576.7009 | 0.61948 | 114.0512 | 9.8737 | 101.9338 | 12.1764 | 25.4545 | 2.8195 | 1885.8896 | 3.1316 | 3.3256 | 135.1632 | 132.8446 | 114.7546 | 133.7784 | 146.8544 | 146.6673 | 1139.652 | 1277.1952 | 1093.2898 | 792.5909 | 1.9423
2024-12-25 | 45648.4167 | 580.6094 | 0.61163 | 119.463 | 8.9142 | 101.2234 | 14.5926 | 26.007 | 7.5558 | 1889.203 | 3.0408 | 3.4857 | 134.388 | 132.0113 | 114.2951 | 135.6287 | 149.4945 | 149.424 | 1116.8527 | 1301.3473 | 1098.6158 | 790.5721 | 5.7607
2024-12-25 | 45648.4583 | 581.8247 | 0.60925 | 126.7727 | 10.5414 | 110.1352 | 13.2515 | 28.5253 | 9.0785 | 1895.902 | 2.6834 | 3.4884 | 135.0461 | 132.6304 | 114.9251 | 137.6508 | 151.4729 | 151.4479 | 1115.1003 | 1321.502 | 1110.2712 | 785.6353 | 6.6201
2024-12-25 | 45648.5 | 584.8107 | 0.59154 | 124.2034 | 8.5588 | 108.5069 | 10.7593 | 24.6796 | 7.093 | 1905.5343 | 2.8031 | 3.6222 | 134.618 | 132.2668 | 114.7161 | 138.9949 | 152.701 | 152.69 | 1107.2152 | 1328.3982 | 1118.9946 | 786.5588 | 9.1798
2024-12-25 | 45648.5417 | 553.2468 | 0.60122 | 116.0878 | 9.5391 | 103.0998 | 14.3199 | 25.7665 | 4.5874 | 1832.875 | 3.3532 | 3.4776 | 133.7953 | 131.6093 | 114.6145 | 137.8221 | 151.0807 | 151.2553 | 1042.3298 | 1229.3679 | 1090.1573 | 742.7214 | 9.1454
2024-12-25 | 45648.5833 | 563.2878 | 0.60164 | 127.9364 | 12.9606 | 102.8358 | 12.2326 | 26.1414 | 8.6432 | 1866.0352 | 2.4638 | 3.6153 | 133.4266 | 131.2506 | 114.2394 | 138.0525 | 151.2049 | 151.5607 | 1052.7579 | 1249.0897 | 1095.2014 | 770.8591 | 7.6616
2024-12-25 | 45648.625 | 576.3174 | 0.59442 | 124.1315 | 11.8564 | 98.1311 | 12.234 | 25.0674 | 14.8491 | 1910.5024 | 2.5675 | 3.6759 | 133.579 | 131.0962 | 114.0772 | 138.9187 | 152.1753 | 152.3462 | 1092.1847 | 1308.8734 | 1142.3604 | 768.1429 | 8.8363
2024-12-25 | 45648.6667 | 576.6328 | 0.59355 | 126.6794 | 18.1805 | 97.7557 | 19.4074 | 25.0746 | 18.8158 | 1904.8309 | 2.5499 | 3.5693 | 133.9904 | 131.439 | 114.5126 | 139.5407 | 152.8554 | 152.8959 | 1083.9668 | 1300.8328 | 1149.4447 | 755.3979 | 8.5072
2024-12-25 | 45648.7083 | 578.4045 | 0.59218 | 127.4458 | 14.6532 | 99.7527 | 18.7269 | 28.2713 | 15.5471 | 1892.2246 | 2.9028 | 3.4991 | 134.262 | 131.7924 | 114.7611 | 139.0659 | 152.1665 | 152.4369 | 1079.8972 | 1287.1041 | 1134.7405 | 757.4931 | 8.8627
2024-12-25 | 45648.75 | 568.7064 | 0.61139 | 132.5482 | 20.1511 | 108.6728 | 26.3002 | 30.4547 | 18.9566 | 1821.3428 | 1.8433 | 3.3806 | 134.993 | 132.7282 | 115.4175 | 140.1445 | 153.1027 | 153.5515 | 1035.9685 | 1220.0475 | 1067.4943 | 753.8676 | 3.4236
2024-12-25 | 45648.7917 | 573.9316 | 0.60185 | 117.7367 | 17.7272 | 86.1044 | 11.1716 | 26.9534 | 9.1532 | 1855.2058 | 2.6403 | 3.5647 | 135.4332 | 133.1874 | 115.5779 | 138.755 | 151.8787 | 152.2547 | 1072.578 | 1252.3262 | 1093.3829 | 761.8307 | 4.3895
2024-12-25 | 45648.8333 | 575.5652 | 0.60897 | 111.8811 | 21.197 | 88.2792 | 17.4689 | 26.2734 | 19.3713 | 1900.1021 | 2.175 | 3.7425 | 135.2155 | 133.0589 | 115.5314 | 139.6729 | 152.2648 | 152.5084 | 1103.8705 | 1301.8107 | 1141.2847 | 758.8269 | 6.3559
2024-12-25 | 45648.875 | 563.206 | 0.60929 | 110.3987 | 18.082 | 88.0222 | 15.3515 | 23.2219 | 15.1505 | 1850.4714 | 2.7745 | 3.7708 | 132.4892 | 130.1991 | 112.9631 | 138.2239 | 151.348 | 151.5059 | 1047.4523 | 1252.6888 | 1111.1093 | 739.3644 | 9.1486
2024-12-25 | 45648.9167 | 490.3746 | 0.60013 | 110.7078 | 15.5547 | 94.7303 | 19.7983 | 21.2805 | 12.1558 | 1612.6074 | 3.6794 | 3.5759 | 130.7843 | 129.4628 | 112.7058 | 134.4993 | 147.0254 | 147.4322 | 858.5215 | 998.7651 | 909.6043 | 703.0176 | 5.2346
2024-12-25 | 45648.9583 | 353.1859 | 0.63502 | 78.639 | 11.9053 | 61.095 | 10.8821 | 7.0042 | 3.4197 | 1396.7384 | 5.752 | 4.7245 | 124.7326 | 124.5144 | 109.4596 | 125.4917 | 137.4517 | 137.6789 | 682.576 | 780.606 | 843.1146 | 553.6622 | 3.8487
2024-12-25 | 45649 | 397.7191 | 0.64658 | 75.5064 | 9.4307 | 75.6009 | 20.8157 | 30.5799 | 4.5091 | 1532.3434 | 5.6391 | 4.1513 | 126.5123 | 124.6516 | 109.5716 | 123.6078 | 135.8141 | 135.6993 | 805.4411 | 901.3209 | 932.247 | 600.0725 | 2.9719
2024-12-26 | 45649.0417 | 332.6066 | 0.65806 | 73.2139 | 9.9188 | 61.3658 | 12.5408 | 7.184 | 2.2219 | 1391.9658 | 6.2597 | 4.9317 | 122.5268 | 121.1713 | 107.6339 | 122.1242 | 134.0022 | 133.9151 | 690.2021 | 782.5035 | 871.3499 | 520.6077 | 2.3622
2024-12-26 | 45649.0833 | 447.2059 | 0.63766 | 113.7334 | 20.0563 | 89.4698 | 17.9413 | 21.5837 | 14.4768 | 1684.9749 | 5.0261 | 4.3998 | 128.6557 | 126.2328 | 110.5085 | 127.3676 | 140.2721 | 140.1256 | 942.2469 | 1066.0175 | 1001.5825 | 683.3516 | 4.3703
2024-12-26 | 45649.125 | 337.3409 | 0.62375 | 71.6297 | 6.659 | 57.9052 | 3.4443 | 3.4308 | 3.6481 | 1405.809 | 6.411 | 5.132 | 120.92 | 120.2731 | 105.8339 | 123.2646 | 135.3313 | 135.1751 | 703.1528 | 807.2106 | 925.4319 | 480.3702 | 4.0237
2024-12-26 | 45649.1667 | 320.7597 | 0.62936 | 63.9537 | 6.1002 | 52.2207 | 5.485 | 0 | 0 | 1303.8622 | 5.6213 | 4.8428 | 118.6867 | 118.2221 | 104.533 | 117.4606 | 129.0881 | 129.1703 | 617.657 | 687.3448 | 826.783 | 477.1021 | 0.5425
2024-12-26 | 45649.2083 | 319.4341 | 0.63438 | 60.7703 | 3.6165 | 52.8969 | 6.8562 | 0 | 0 | 1281.6676 | 5.3136 | 4.5584 | 117.369 | 117.5379 | 103.6164 | 116.1972 | 127.7622 | 128.094 | 594.8469 | 656.7946 | 798.5349 | 483.1295 | 0.17032
2024-12-26 | 45649.25 | 429.0151 | 0.65806 | 107.1133 | 9.0791 | 96.7376 | 13.4531 | 27.6623 | 8.457 | 1701.7739 | 5.3889 | 4.3874 | 124.5582 | 122.3174 | 106.7731 | 119.9988 | 132.942 | 132.9053 | 943.3678 | 1030.6708 | 1016.6433 | 685.1494 | 1.2137
2024-12-26 | 45649.2917 | 564.1105 | 0.61846 | 111.2577 | 9.5725 | 101.1578 | 15.5371 | 29.6487 | 1.2726 | 1979.3029 | 4.6195 | 4.0711 | 131.7803 | 129.2664 | 111.2152 | 132.8722 | 146.9824 | 146.8028 | 1199.3547 | 1394.7542 | 1180.2015 | 799.1268 | 9.4696
2024-12-26 | 45649.3333 | 577.2842 | 0.61038 | 119.2119 | 8.8087 | 114.62 | 10.0164 | 17.3923 | 0.078804 | 1927.7684 | 4.0927 | 3.816 | 131.5728 | 129.2631 | 111.4629 | 135.1445 | 149.0805 | 149.3497 | 1141.501 | 1350.1349 | 1129.6688 | 798.111 | 10.5338
2024-12-26 | 45649.375 | 578.446 | 0.61835 | 129.9711 | 14.2694 | 117.5339 | 14.5552 | 21.0523 | 10.3162 | 1912.3601 | 3.7064 | 3.798 | 131.8846 | 129.4418 | 111.6061 | 136.5109 | 150.4047 | 150.7624 | 1125.838 | 1347.0308 | 1116.255 | 796.0829 | 10.2536
2024-12-26 | 45649.4167 | 586.2916 | 0.62361 | 133.5202 | 14.5492 | 124.2116 | 14.9992 | 26.9702 | 14.2701 | 1906.7997 | 3.0231 | 3.6714 | 133.8608 | 131.3863 | 113.4173 | 139.1131 | 153.0326 | 153.553 | 1133.748 | 1362.5182 | 1111.637 | 795.1907 | 10.586
2024-12-26 | 45649.4583 | 585.08 | 0.62457 | 131.9068 | 14.515 | 129.6319 | 18.0363 | 29.5629 | 15.2002 | 1899.876 | 3.6058 | 3.6805 | 135.0744 | 132.4603 | 114.6419 | 140.9943 | 154.9386 | 155.3419 | 1123.2948 | 1355.9926 | 1103.6854 | 796.2269 | 13.7328
2024-12-26 | 45649.5 | 586.8994 | 0.63162 | 128.149 | 13.1207 | 112.9947 | 11.0336 | 31.4693 | 15.3731 | 1926.2625 | 3.6994 | 3.7121 | 135.5482 | 133.0202 | 115.1556 | 142.4626 | 156.2655 | 156.6922 | 1136.8364 | 1390.7595 | 1138.0049 | 788.2524 | 14.8968
2024-12-26 | 45649.5417 | 582.9919 | 0.63536 | 114.2964 | 14.4337 | 106.2082 | 14.2151 | 27.8702 | 14.7982 | 1895.9304 | 3.0559 | 3.6141 | 136.0587 | 134.0117 | 116.0747 | 144.1709 | 157.2249 | 157.9376 | 1120.6234 | 1363.8231 | 1108.9841 | 786.9317 | 10.9271
2024-12-26 | 45649.5833 | 451.8234 | 0.61685 | 87.9066 | 8.7692 | 74.9592 | 8.7247 | 10.1792 | 3.5269 | 1597.2023 | 4.7271 | 4.3052 | 129.9147 | 129.0703 | 112.9758 | 139.2615 | 151.4187 | 152.2584 | 832.6544 | 1013.7922 | 920.3469 | 676.8352 | 11.7937
2024-12-26 | 45649.625 | 416.2345 | 0.64644 | 97.1787 | 10.207 | 83.4591 | 9.6745 | 3.6551 | 0.88342 | 1450.2916 | 4.5535 | 3.9988 | 127.8511 | 126.3488 | 112.3393 | 131.2118 | 142.5436 | 143.1261 | 724.9786 | 835.6036 | 860.4462 | 589.8198 | 3.0434
2024-12-26 | 45649.6667 | 538.7762 | 0.63932 | 128.6597 | 17.2504 | 114.6062 | 20.6109 | 28.4731 | 22.7835 | 1763.2915 | 3.235 | 3.31 | 135.8629 | 133.213 | 116.9822 | 135.9229 | 148.3561 | 148.5873 | 1004.5394 | 1140.4939 | 1001.8821 | 761.4094 | 4.3261
2024-12-26 | 45649.7083 | 581.6546 | 0.62485 | 130.5807 | 21.8857 | 116.2683 | 18.3155 | 30.0431 | 24.2356 | 1894.5698 | 2.6481 | 3.458 | 137.0005 | 134.5917 | 116.983 | 141.6382 | 155.002 | 155.3212 | 1104.5166 | 1315.9097 | 1100.4696 | 794.0717 | 9.3118
2024-12-26 | 45649.75 | 582.3913 | 0.61901 | 131.8365 | 16.0449 | 127.3786 | 15.5843 | 28.7999 | 22.1032 | 1900.6671 | 2.7535 | 3.5479 | 136.0655 | 133.7319 | 116.0803 | 141.8858 | 155.1204 | 155.7966 | 1105.3138 | 1329.7299 | 1111.1536 | 789.5171 | 10.6844
2024-12-26 | 45649.7917 | 551.4011 | 0.63104 | 128.1239 | 17.4932 | 122.0475 | 19.1806 | 30.9569 | 26.7708 | 1806.2117 | 2.9387 | 3.4457 | 134.2512 | 132.2621 | 114.7743 | 141.0336 | 153.9508 | 154.6638 | 1021.0854 | 1222.0002 | 1024.5045 | 781.7046 | 10.2511
2024-12-26 | 45649.8333 | 578.6483 | 0.62403 | 123.8023 | 14.4846 | 118.4265 | 16.4701 | 24.3112 | 16.7265 | 1889.2782 | 2.8503 | 3.5346 | 134.9922 | 132.6422 | 114.676 | 141.1608 | 154.5741 | 155.0583 | 1106.0929 | 1335.5977 | 1106.8013 | 782.4662 | 11.8754
2024-12-26 | 45649.875 | 507.055 | 0.6317 | 97.0611 | 12.5759 | 76.3994 | 14.3002 | 11.6979 | 6.816 | 1652.1881 | 3.5338 | 3.5962 | 132.9029 | 131.7279 | 114.1967 | 138.8416 | 151.2676 | 151.8491 | 912.3453 | 1083.4377 | 953.262 | 698.9468 | 8.1491
2024-12-26 | 45649.9167 | 460.8119 | 0.6458 | 99.1611 | 13.4398 | 79.291 | 18.5289 | 11.59 | 6.0124 | 1558.9171 | 4.0797 | 3.699 | 129.7301 | 128.9722 | 112.3285 | 133.5334 | 145.4621 | 146.304 | 817.3609 | 952.1047 | 875.3097 | 683.6227 | 5.354
2024-12-26 | 45649.9583 | 484.9464 | 0.6514 | 116.8364 | 12.7396 | 97.9834 | 18.1328 | 12.0632 | 7.3961 | 1681.6812 | 3.9743 | 3.8946 | 130.4433 | 128.8465 | 112.0778 | 132.1318 | 145.2326 | 145.4919 | 930.4437 | 1080.1809 | 989.8246 | 691.8707 | 7.5905
2024-12-26 | 45650 | 456.1546 | 0.65609 | 113.9934 | 17.3384 | 91.451 | 19.2484 | 13.6543 | 7.7726 | 1593.2504 | 4.0099 | 3.958 | 127.924 | 126.6958 | 110.2376 | 130.9284 | 144.0061 | 144.1949 | 845.9283 | 985.6161 | 901.3992 | 691.8708 | 7.0085
2024-12-27 | 45650.0417 | 524.1496 | 0.66248 | 136.7245 | 11.9955 | 132.2199 | 19.1384 | 27.1052 | 15.0384 | 1907.9893 | 4.2016 | 3.9972 | 131.7003 | 129.1135 | 111.9386 | 133.3279 | 147.3702 | 147.5139 | 1103.6002 | 1302.0765 | 1113.1591 | 794.8416 | 13.5683
2024-12-27 | 45650.0833 | 524.1956 | 0.6415 | 123.121 | 7.5621 | 113.0923 | 14.025 | 16.3408 | 11.2236 | 1913.1747 | 4.5121 | 4.4276 | 128.8444 | 126.6723 | 109.3349 | 136.6504 | 150.9752 | 151.0968 | 1093.1254 | 1350.5032 | 1135.5128 | 777.6948 | 21.7803
2024-12-27 | 45650.125 | 339.1004 | 0.65653 | 69.5535 | 2.9505 | 58.0719 | 6.0387 | 1.625 | 0.96478 | 1376.3636 | 5.3021 | 4.9628 | 118.3418 | 118.0331 | 103.6666 | 125.1029 | 137.2443 | 137.6099 | 647.9105 | 770.3232 | 842.1509 | 534.25 | 7.6555
2024-12-27 | 45650.1667 | 312.2394 | 0.66752 | 59.8433 | 0.18682 | 53.9386 | 5.4541 | 8.277 | 0 | 1288.007 | 5.0106 | 4.8206 | 117.455 | 117.3989 | 103.6155 | 117.5165 | 128.9263 | 129.5643 | 603.8198 | 683.2108 | 807.5143 | 480.4902 | 0.75686
2024-12-27 | 45650.2083 | 316.4261 | 0.66172 | 59.7738 | 0.34687 | 55.3637 | 5.8979 | 0 | 0 | 1286.2047 | 4.9591 | 4.7031 | 117.7937 | 117.7049 | 103.8175 | 117.4702 | 129.1116 | 129.6882 | 606.2427 | 680.2385 | 796.9837 | 489.2341 | 0.126
2024-12-27 | 45650.25 | 340.3808 | 0.66636 | 75.0695 | 3.2997 | 70.8096 | 9.7774 | 14.017 | 8.2277 | 1393.2876 | 4.9901 | 4.7907 | 119.1927 | 118.4104 | 104.3458 | 117.7319 | 129.639 | 130.0992 | 685.396 | 759.6231 | 845.8397 | 547.4206 | 0.043913
2024-12-27 | 45650.2917 | 520.5418 | 0.65618 | 127.6636 | 9.5118 | 123.6253 | 16.175 | 23.7479 | 14.0459 | 1906.2434 | 4.3084 | 4.2469 | 131.2306 | 128.2769 | 111.1302 | 130.2725 | 144.2338 | 144.0971 | 1153.1962 | 1317.2733 | 1129.7085 | 776.5466 | 8.4435
2024-12-27 | 45650.3333 | 576.2872 | 0.62928 | 123.1094 | 11.8926 | 104.8794 | 15.1786 | 13.8223 | 15.0842 | 1916.1451 | 2.8883 | 3.6847 | 132.4951 | 130.2095 | 112.189 | 136.6966 | 150.5878 | 150.5579 | 1148.5321 | 1353.9128 | 1121.3024 | 794.8419 | 8.8121
2024-12-27 | 45650.375 | 577.9992 | 0.62499 | 127.7328 | 11.9225 | 108.4916 | 6.7269 | 24.5125 | 19.3008 | 1904.6348 | 3.2467 | 3.733 | 131.9355 | 129.4751 | 111.7235 | 136.7134 | 150.9734 | 151.1449 | 1112.3881 | 1338.3461 | 1114.4805 | 790.1497 | 11.9252
2024-12-27 | 45650.4167 | 578.8525 | 0.62401 | 128.6872 | 12.4352 | 113.1372 | 13.0642 | 25.3029 | 22.6086 | 1903.4717 | 2.6378 | 3.5811 | 133.2458 | 130.7716 | 113.0249 | 138.4631 | 152.4273 | 152.7795 | 1113.1013 | 1343.7469 | 1117.0767 | 786.4008 | 10.8953
2024-12-27 | 45650.4583 | 545.4242 | 0.63146 | 120.1819 | 18.199 | 111.7444 | 20.8449 | 21.8508 | 18.7665 | 1839.5892 | 3.3505 | 3.5998 | 132.603 | 130.314 | 113.0564 | 138.8976 | 152.2406 | 152.759 | 1055.6324 | 1272.4343 | 1085.3339 | 754.2513 | 13.3823
2024-12-27 | 45650.5 | 575.9076 | 0.63128 | 131.613 | 18.0375 | 118.1889 | 17.6108 | 28.9634 | 23.5863 | 1931.8711 | 3.3809 | 3.749 | 134.5586 | 132.046 | 114.477 | 143.1453 | 156.587 | 157.3223 | 1134.5946 | 1415.6731 | 1147.583 | 784.2681 | 17.96
2024-12-27 | 45650.5417 | 535.8677 | 0.60964 | 112.8222 | 15.4669 | 95.4307 | 13.6256 | 21.9607 | 17.939 | 1840.9972 | 3.8316 | 3.9924 | 132.8489 | 130.8657 | 113.7023 | 144.2443 | 157.2483 | 157.9404 | 1039.5153 | 1322.0082 | 1108.6168 | 732.3802 | 18.826
2024-12-27 | 45650.5833 | 360.9364 | 0.63218 | 57.7681 | 6.4722 | 58.2686 | 10.4244 | 2.5268 | 0.42198 | 1370.5995 | 4.5678 | 4.4559 | 122.853 | 122.5826 | 108.3445 | 131.6703 | 142.934 | 144.0735 | 638.1866 | 774.8633 | 844.3406 | 526.2903 | 7.0902
2024-12-27 | 45650.625 | 483.5376 | 0.6481 | 109.1651 | 14.6956 | 102.5441 | 24.5485 | 26.1122 | 18.037 | 1698.6855 | 3.7734 | 3.6431 | 131.7437 | 129.172 | 113.853 | 131.7375 | 143.8181 | 144.635 | 934.3615 | 1067.3784 | 984.9966 | 713.6791 | 5.6577
2024-12-27 | 45650.6667 | 584.5497 | 0.62422 | 128.6796 | 15.5171 | 120.9137 | 14.9297 | 30.6837 | 26.2681 | 1928.5612 | 2.7703 | 3.4832 | 136.7712 | 134.2717 | 117.015 | 142.6316 | 155.9814 | 156.3574 | 1126.5807 | 1380.0454 | 1133.4457 | 795.0965 | 11.7727
2024-12-27 | 45650.7083 | 585.5972 | 0.62519 | 135.2473 | 11.7509 | 122.5492 | 19.066 | 35.2219 | 20.3768 | 1926.6476 | 2.9625 | 3.363 | 136.3666 | 133.7798 | 116.5051 | 143.2486 | 156.5945 | 156.9798 | 1116.5581 | 1376.615 | 1150.0415 | 776.5876 | 12.1294
2024-12-27 | 45650.75 | 586.1188 | 0.6276 | 132.6833 | 9.4123 | 125.7349 | 19.0134 | 37.3954 | 23.8322 | 1926.6989 | 2.6424 | 3.2932 | 136.0877 | 133.5611 | 116.2465 | 143.3077 | 156.5945 | 156.9817 | 1113.5166 | 1377.2069 | 1152.1506 | 774.5813 | 11.0734
2024-12-27 | 45650.7917 | 581.7342 | 0.62517 | 108.5666 | 8.4526 | 95.6702 | 12.7164 | 37.6112 | 16.8855 | 1908.1204 | 2.762 | 3.4261 | 134.5886 | 132.2594 | 114.7661 | 143.01 | 156.0607 | 156.4707 | 1094.9762 | 1363.0853 | 1137.5322 | 770.5823 | 10.2232
2024-12-27 | 45650.8333 | 586.0602 | 0.6253 | 112.5526 | 6.5916 | 96.7253 | 9.0397 | 32.5908 | 17.9579 | 1936.1115 | 2.5452 | 3.495 | 135.0461 | 132.7825 | 114.7791 | 143.3165 | 156.1546 | 156.5689 | 1133.8223 | 1406.8318 | 1158.0377 | 778.0728 | 9.3441
2024-12-27 | 45650.875 | 586.4168 | 0.61883 | 112.5525 | 7.4375 | 97.4225 | 11.4853 | 31.1249 | 23.1387 | 1929.6292 | 2.499 | 3.6277 | 133.5328 | 131.0337 | 113.3057 | 142.9884 | 156.2397 | 156.5262 | 1114.7518 | 1401.8918 | 1149.1685 | 780.4892 | 11.8181
2024-12-27 | 45650.9167 | 551.9835 | 0.61323 | 109.5733 | 13.7829 | 97.5865 | 12.0475 | 25.3074 | 22.7783 | 1829.0785 | 2.7079 | 3.8297 | 130.5366 | 128.5939 | 111.1636 | 142.5898 | 155.6712 | 155.8962 | 1010.9682 | 1286.3807 | 1067.975 | 761.1198 | 12.6576
2024-12-27 | 45650.9583 | 483.1417 | 0.62041 | 97.32 | 15.4432 | 80.4001 | 12.8392 | 8.8949 | 13.5857 | 1630.5562 | 3.2425 | 3.9119 | 127.0587 | 125.7216 | 109.227 | 137.6134 | 149.955 | 150.2401 | 853.2659 | 1056.6396 | 968.2143 | 662.3547 | 8.1576
2024-12-27 | 45651 | 501.959 | 0.61869 | 103.1197 | 12.0701 | 83.4209 | 12.5363 | 12.1378 | 8.7687 | 1671.067 | 3.4378 | 3.6341 | 129.1525 | 127.3005 | 110.5275 | 133.6741 | 146.5533 | 146.5233 | 914.4595 | 1079.2289 | 985.4142 | 685.6282 | 6.2517
2024-12-28 | 45651.0417 | 411.5919 | 0.6272 | 107.4205 | 12.0854 | 90.0271 | 11.3244 | 5.4911 | 7.8875 | 1431.8467 | 3.9065 | 4.1297 | 125.3242 | 124.5074 | 109.2616 | 129.6422 | 141.709 | 141.9742 | 714.6214 | 835.0817 | 850.6378 | 581.1851 | 2.1721
2024-12-28 | 45651.0833 | 354.0387 | 0.64585 | 84.8139 | 8.1098 | 78.373 | 4.6574 | 5.9584 | 2.3408 | 1356.3739 | 4.6059 | 4.4616 | 121.093 | 120.1577 | 106.3857 | 124.09 | 135.849 | 136.2277 | 637.5567 | 729.089 | 789.8361 | 566.531 | 1.3959
2024-12-28 | 45651.125 | 350.2201 | 0.64918 | 77.8527 | 7.0251 | 72.2973 | 7.4495 | 1.7269 | 4.1736 | 1335.541 | 4.0667 | 4.3235 | 119.2984 | 118.8529 | 104.8925 | 121.1684 | 132.7018 | 133.528 | 616.3539 | 693.8336 | 778.0344 | 557.5117 | 0.43382
2024-12-28 | 45651.1667 | 352.8362 | 0.63887 | 76.5621 | 6.0913 | 71.2581 | 6.0696 | 2.0134 | 0 | 1338.1046 | 4.1367 | 4.3266 | 120.0588 | 119.925 | 105.4532 | 120.878 | 132.5799 | 133.6235 | 625.7605 | 696.6152 | 777.7457 | 560.3517 | 0.22374
2024-12-28 | 45651.2083 | 333.6042 | 0.64617 | 73.9763 | 4.9362 | 70.219 | 5.5662 | 1.9857 | 0 | 1312.8966 | 4.7574 | 4.4284 | 120.7368 | 119.8415 | 106.4475 | 120.168 | 132.1017 | 132.9637 | 618.0971 | 681.8226 | 778.6615 | 534.23 | 0.31586
2024-12-28 | 45651.25 | 313.4242 | 0.65882 | 60.6945 | 3.3633 | 61.3132 | 2.2655 | 0.024237 | 0 | 1267.2998 | 4.8794 | 4.4906 | 119.2168 | 118.7821 | 105.5088 | 117.4857 | 128.9791 | 129.2802 | 587.8291 | 649.1725 | 783.3996 | 483.9181 | 0.3125
2024-12-28 | 45651.2917 | 334.3368 | 0.67643 | 74.6861 | 5.6563 | 68.6651 | 8.2843 | 6.1772 | 1.7109 | 1327.9708 | 4.724 | 4.3191 | 121.8024 | 121.9831 | 107.6144 | 120.6121 | 130.3589 | 131.2453 | 636.6373 | 698.1292 | 785.0566 | 542.9221 | 0.47158
2024-12-28 | 45651.3333 | 522.4712 | 0.66411 | 133.3349 | 12.192 | 114.8952 | 16.0779 | 15.9193 | 17.1797 | 1789.1105 | 3.439 | 3.4873 | 133.016 | 130.1546 | 113.7463 | 129.5462 | 142.9756 | 142.8976 | 1049.4641 | 1159.0181 | 1026.2065 | 762.9167 | 2.3323
2024-12-28 | 45651.375 | 576.9634 | 0.63236 | 120.6197 | 12.7985 | 99.2167 | 8.1158 | 11.1703 | 8.9359 | 1903.7134 | 2.5892 | 3.5951 | 133.9487 | 131.7874 | 113.9651 | 136.6261 | 150.6211 | 150.4956 | 1131.8259 | 1326.9628 | 1139.6127 | 764.1483 | 6.7342
2024-12-28 | 45651.4167 | 545.567 | 0.62521 | 110.8783 | 6.5709 | 85.5818 | 13.5698 | 8.3781 | 0 | 1817.4706 | 3.0637 | 3.6981 | 132.6149 | 131.276 | 113.7333 | 137.9554 | 151.1324 | 151.483 | 1046.6743 | 1250.1383 | 1094.342 | 723.1332 | 8.0732
2024-12-28 | 45651.4583 | 426.6293 | 0.6229 | 83.6138 | 7.7331 | 68.6914 | 14.01 | 1.6848 | 0 | 1470.0364 | 4.0018 | 3.9656 | 125.9634 | 125.3618 | 110.342 | 130.9572 | 143.1021 | 143.5782 | 737.1503 | 860.2929 | 890.4188 | 579.5935 | 3.7112
2024-12-28 | 45651.5 | 317.4679 | 0.65407 | 46.0732 | 4.6956 | 45.8998 | 7.3054 | 0 | 0 | 1219.7933 | 4.5018 | 4.4452 | 119.71 | 120.2506 | 106.6667 | 122.4604 | 133.4381 | 134.2624 | 554.4908 | 628.0116 | 776.4702 | 443.3241 | 0.70761
2024-12-28 | 45651.5417 | 317.7168 | 0.6463 | 53.7659 | 2.9749 | 54.0337 | 8.5481 | 4.0861 | 0 | 1259.3179 | 4.5729 | 4.4332 | 119.2527 | 119.502 | 106.0982 | 119.7843 | 130.834 | 131.4626 | 573.3541 | 637.3956 | 771.6081 | 487.7134 | 0.2839
2024-12-28 | 45651.5833 | 325.8584 | 0.67566 | 57.5723 | 3.8518 | 58.3471 | 10.8276 | 6.2756 | 0 | 1323.3547 | 4.6322 | 4.5008 | 119.2985 | 119.7132 | 105.566 | 120.2038 | 131.6215 | 132.5638 | 611.0751 | 677.5579 | 770.6996 | 552.6454 | 0.23438
2024-12-28 | 45651.625 | 435.4482 | 0.6664 | 99.5923 | 10.0765 | 78.7103 | 14.7252 | 22.9591 | 9.3662 | 1567.1064 | 4.051 | 3.8138 | 127.4152 | 125.8912 | 110.379 | 123.3144 | 136.1646 | 136.6191 | 849.127 | 916.956 | 922.8729 | 644.2313 | 0.23438
2024-12-28 | 45651.6667 | 561.8582 | 0.64092 | 129.1412 | 13.4888 | 112.1873 | 18.2308 | 35.0717 | 25.7155 | 1866.6472 | 3.239 | 3.3902 | 135.4362 | 132.8633 | 115.4104 | 132.8232 | 147.4261 | 147.3344 | 1119.3717 | 1246.2051 | 1068.2419 | 798.386 | 2.5986
2024-12-28 | 45651.7083 | 586.395 | 0.63825 | 137.1176 | 13.6208 | 129.8664 | 23.9324 | 39.6323 | 16.7225 | 1908.1119 | 2.3158 | 3.1981 | 136.478 | 134.1895 | 115.8166 | 135.9288 | 150.7148 | 150.8885 | 1162.6431 | 1324.2732 | 1121.0081 | 787.1052 | 4.7378
2024-12-28 | 45651.75 | 589.0007 | 0.63466 | 134.2635 | 11.139 | 120.9183 | 22.0749 | 38.7959 | 14.9379 | 1935.8867 | 2.5792 | 3.327 | 135.3449 | 133.1458 | 114.8159 | 136.6643 | 151.7627 | 152.0044 | 1163.7826 | 1364.3926 | 1143.5796 | 792.3302 | 9.1755
2024-12-28 | 45651.7917 | 584.6963 | 0.64037 | 115.3013 | 9.5208 | 94.5246 | 16.8897 | 37.0237 | 11.9125 | 1939.5947 | 2.5951 | 3.3879 | 133.9805 | 131.8871 | 113.6076 | 137.7579 | 152.1878 | 152.7661 | 1152.7184 | 1378.4308 | 1149.255 | 790.3516 | 12.1127
2024-12-28 | 45651.8333 | 588.5352 | 0.64292 | 122.9498 | 9.2546 | 100.098 | 14.5849 | 33.534 | 15.5571 | 1974.0231 | 2.495 | 3.5336 | 134.5584 | 132.2484 | 114.1325 | 138.4718 | 152.0671 | 153.1597 | 1188.8357 | 1418.0054 | 1186.1641 | 787.8711 | 10.6135
2024-12-28 | 45651.875 | 591.7562 | 0.63668 | 122.8549 | 11.0967 | 104.7421 | 16.203 | 36.6155 | 16.8499 | 1980.6602 | 2.4714 | 3.6136 | 133.2897 | 130.5858 | 112.7184 | 138.3355 | 153.034 | 153.2814 | 1178.2434 | 1426.5719 | 1190.791 | 789.8731 | 12.346
2024-12-28 | 45651.9167 | 579.0645 | 0.63331 | 127.1967 | 9.1806 | 105.3734 | 12.9242 | 34.3213 | 20.2465 | 1916.4772 | 3.063 | 3.575 | 133.0468 | 130.4494 | 112.6318 | 138.8439 | 153.399 | 153.7641 | 1122.0038 | 1371.5098 | 1130.5115 | 785.9656 | 13.8423
2024-12-28 | 45651.9583 | 555.8571 | 0.6425 | 130.8033 | 16.4767 | 114.68 | 19.9689 | 32.7646 | 29.1851 | 1835.6198 | 2.8123 | 3.5203 | 134.499 | 132.4543 | 114.6954 | 136.7173 | 150.9087 | 151.3649 | 1044.5581 | 1271.3751 | 1058.7721 | 776.8384 | 10.4257
2024-12-28 | 45652 | 567.0187 | 0.64585 | 136.5906 | 16.9553 | 119.6693 | 17.8267 | 34.0444 | 30.5942 | 1871.1703 | 2.425 | 3.4801 | 135.3792 | 133.1395 | 115.2645 | 137.3192 | 151.4439 | 152 | 1073.1809 | 1317.6327 | 1096.5238 | 774.6177 | 9.4252
2024-12-29 | 45652.0417 | 577.1667 | 0.6424 | 132.2132 | 14.306 | 115.5497 | 16.8502 | 34.7773 | 30.729 | 1936.1559 | 2.7636 | 3.6027 | 135.1662 | 132.6278 | 114.8219 | 136.6935 | 151.0311 | 151.3437 | 1119.8776 | 1386.3448 | 1166.1595 | 769.9859 | 11.0904
2024-12-29 | 45652.0833 | 575.8016 | 0.64353 | 131.0827 | 12.902 | 111.2757 | 15.2575 | 34.4333 | 30.0075 | 1937.7021 | 2.7853 | 3.6168 | 133.9447 | 131.1505 | 113.4645 | 137.4495 | 152.0707 | 151.9939 | 1118.2059 | 1397.9619 | 1166.4888 | 771.233 | 12.299
2024-12-29 | 45652.125 | 573.088 | 0.64786 | 115.8093 | 12.3588 | 95.3872 | 16.3596 | 31.3383 | 26.5411 | 1924.8958 | 2.566 | 3.6281 | 133.631 | 131.1519 | 113.2105 | 137.9057 | 152.0521 | 152.1004 | 1112.7006 | 1396.104 | 1154.6229 | 770.2606 | 10.4072
2024-12-29 | 45652.1667 | 576.0742 | 0.64419 | 122.1155 | 9.9867 | 103.2871 | 13.5975 | 33.4937 | 28.9798 | 1945.8573 | 2.599 | 3.7061 | 133.1839 | 130.4519 | 112.7562 | 137.1159 | 151.5169 | 151.3486 | 1126.6498 | 1421.7692 | 1176.7101 | 769.1553 | 12.6974
2024-12-29 | 45652.2083 | 529.8712 | 0.62941 | 114.7597 | 10.4951 | 93.5488 | 10.203 | 28.3962 | 20.6326 | 1785.8176 | 3.1613 | 3.7881 | 130.9008 | 128.8653 | 111.5743 | 136.8661 | 150.9987 | 150.8548 | 990.115 | 1267.5817 | 1053.8828 | 731.9293 | 14.233
2024-12-29 | 45652.25 | 508.1758 | 0.6571 | 116.4592 | 14.0818 | 99.9497 | 20.1732 | 26.1797 | 18.5902 | 1702.4811 | 3.3032 | 3.3451 | 130.0229 | 128.0715 | 111.1309 | 132.0906 | 145.7959 | 145.8177 | 923.7301 | 1134.3545 | 969.2845 | 733.1863 | 8.9949
2024-12-29 | 45652.2917 | 580.8749 | 0.649 | 137.9139 | 13.7663 | 120.4718 | 15.1741 | 36.0721 | 28.7855 | 1904.4875 | 2.3184 | 3.4624 | 134.32 | 131.8007 | 113.4529 | 135.6742 | 150.3481 | 150.2097 | 1118.6093 | 1378.9225 | 1110.3224 | 794.1642 | 9.7583
2024-12-29 | 45652.3333 | 586.385 | 0.64184 | 119.8461 | 9.6367 | 119.4008 | 15.0653 | 34.7708 | 29.5581 | 1963.0393 | 3.1469 | 3.751 | 132.8503 | 130.3697 | 111.8364 | 136.0427 | 151.1906 | 150.9143 | 1149.2571 | 1443.0109 | 1175.4734 | 787.5421 | 13.1861
2024-12-29 | 45652.375 | 576.3452 | 0.63682 | 111.4642 | 10.1379 | 100.3574 | 12.2062 | 18.3456 | 12.5364 | 1946.7172 | 3.7401 | 3.8105 | 132.3152 | 129.909 | 111.6135 | 136.7227 | 151.4021 | 151.4849 | 1119.384 | 1424.8708 | 1166.0513 | 780.6838 | 12.3125
2024-12-29 | 45652.4167 | 565.5192 | 0.62986 | 108.4133 | 19.0763 | 88.3419 | 17.5185 | 18.3862 | 6.4049 | 1940.8258 | 3.5108 | 3.86 | 131.3591 | 129.4677 | 111.3914 | 136.4034 | 150.2224 | 150.5226 | 1094.0156 | 1390.2726 | 1159.5929 | 781.2559 | 11.5816
2024-12-29 | 45652.4583 | 539.283 | 0.64492 | 109.0732 | 18.764 | 94.2688 | 23.9831 | 16.9317 | 4.937 | 1892.2648 | 4.0134 | 3.8802 | 130.9051 | 128.6049 | 111.1277 | 134.9893 | 148.8046 | 148.6139 | 1063.5428 | 1346.7078 | 1142.7081 | 749.5403 | 15.4992
2024-12-29 | 45652.5 | 575.4349 | 0.62638 | 114.1455 | 21.1465 | 98.0709 | 22.223 | 12.8591 | 9.4497 | 1934.1073 | 3.3322 | 3.8074 | 133.146 | 130.8984 | 112.9143 | 140.1066 | 154.0971 | 154.0324 | 1102.4465 | 1433.1893 | 1158.0037 | 776.0896 | 15.6869
2024-12-29 | 45652.5417 | 402.3954 | 0.63129 | 76.9792 | 11.9116 | 66.1926 | 13.2305 | 2.8698 | 0.7635 | 1516.5676 | 4.8172 | 4.6092 | 125.4228 | 125.2859 | 109.2402 | 134.7267 | 147.1517 | 147.7729 | 743.5751 | 978.0529 | 902.2719 | 614.3282 | 14.0113
2024-12-29 | 45652.5833 | 339.6362 | 0.66751 | 65.1166 | 6.1273 | 63.043 | 11.7567 | 3.9866 | 1.081 | 1384.856 | 4.9386 | 4.7733 | 120.7638 | 120.8249 | 106.4187 | 125.5065 | 137.011 | 137.9738 | 631.9771 | 792.0625 | 820.7648 | 564.1191 | 6.8195
2024-12-29 | 45652.625 | 321.1681 | 0.67918 | 53.7271 | 6.1349 | 55.4108 | 13.4694 | 2.0963 | 0 | 1330.5803 | 4.7271 | 4.6785 | 119.8948 | 120.2859 | 106.1489 | 122.7506 | 133.929 | 134.9399 | 586.3505 | 715.3833 | 772.2193 | 558.3501 | 2.8857
2024-12-29 | 45652.6667 | 418.8473 | 0.69315 | 94.794 | 13.355 | 83.2367 | 21.0154 | 15.5149 | 9.7246 | 1554.1876 | 3.7385 | 3.7968 | 126.4153 | 125.1634 | 110.1133 | 125.1524 | 136.9788 | 137.6855 | 769.164 | 903.7427 | 876.8633 | 677.3463 | 1.8884
2024-12-29 | 45652.7083 | 562.3589 | 0.64176 | 126.911 | 14.4899 | 106.4298 | 20.8305 | 16.309 | 7.871 | 1874.7024 | 3.517 | 3.3882 | 138.1876 | 136.1225 | 118.3478 | 136.5521 | 150.2217 | 150.2599 | 1086.369 | 1296.1351 | 1099.566 | 775.1045 | 9.0284
2024-12-29 | 45652.75 | 563.9877 | 0.6579 | 134.5895 | 21.4874 | 113.6147 | 31.0914 | 22.6147 | 13.5432 | 1891.7661 | 2.8218 | 3.2941 | 136.6778 | 134.5427 | 116.8373 | 136.5622 | 150.4066 | 150.6548 | 1082.2054 | 1321.7015 | 1098.9514 | 792.8044 | 9.0084
2024-12-29 | 45652.7917 | 580.8149 | 0.65422 | 128.7931 | 20.7504 | 104.978 | 22.6793 | 17.6152 | 9.9195 | 1928.3517 | 2.6676 | 3.5252 | 136.7755 | 134.4625 | 116.4396 | 139.2548 | 153.3894 | 153.6334 | 1117.7506 | 1401.4447 | 1149.9222 | 778.417 | 10.6364
2024-12-29 | 45652.8333 | 580.2929 | 0.65441 | 114.3919 | 16.9835 | 88.5463 | 22.9985 | 18.7261 | 4.5388 | 1916.465 | 2.7918 | 3.4047 | 136.8612 | 134.9706 | 116.3481 | 139.6304 | 153.1411 | 153.5285 | 1122.4321 | 1393.4766 | 1141.9205 | 774.5399 | 9.6843
2024-12-29 | 45652.875 | 580.0718 | 0.63733 | 116.0097 | 20.216 | 91.7366 | 22.4501 | 15.2159 | 8.427 | 1913.2092 | 2.5787 | 3.5714 | 135.0219 | 132.8099 | 114.6905 | 138.1801 | 152.3975 | 152.458 | 1102.548 | 1382.642 | 1134.1599 | 779.0489 | 10.708
2024-12-29 | 45652.9167 | 579.1471 | 0.63515 | 118.3999 | 21.7072 | 93.1385 | 19.2237 | 15.422 | 9.9152 | 1926.0272 | 2.5081 | 3.7206 | 134.3434 | 132.0588 | 114.0069 | 138.1923 | 152.2413 | 152.442 | 1103.5558 | 1399.4993 | 1161.6849 | 764.3578 | 10.2255
2024-12-29 | 45652.9583 | 553.0837 | 0.64815 | 123.1126 | 22.4921 | 97.3815 | 24.0244 | 22.8525 | 6.744 | 1828.0736 | 2.789 | 3.5184 | 132.6645 | 130.7829 | 113.0494 | 135.5604 | 149.5212 | 149.6345 | 1007.1645 | 1266.5736 | 1071.7012 | 756.3552 | 8.6672
2024-12-29 | 45653 | 471.6971 | 0.61445 | 101.2234 | 16.4173 | 77.9832 | 19.2079 | 9.498 | 2.5492 | 1652.7716 | 3.9326 | 4.2046 | 129.7165 | 128.9984 | 112.1119 | 132.7024 | 146.0756 | 146.0635 | 861.0853 | 1100.3846 | 991.1904 | 661.571 | 10.019
2024-12-30 | 45653.0417 | 331.2681 | 0.66669 | 68.8244 | 5.5814 | 61.2304 | 9.0754 | 0.16238 | 0 | 1350.1412 | 4.9389 | 4.7333 | 117.967 | 118.0173 | 104.2028 | 121.1405 | 133.3481 | 133.8653 | 584.6564 | 738.8747 | 785.5825 | 564.5269 | 4.3272
2024-12-30 | 45653.0833 | 325.6768 | 0.68788 | 67.1319 | 4.6539 | 63.1482 | 10.2972 | 0 | 0 | 1348.3497 | 4.6207 | 4.6781 | 118.6022 | 118.2341 | 104.6325 | 116.7775 | 129.0418 | 129.4593 | 598.1932 | 713.8817 | 783.7084 | 564.6326 | 0.82377
2024-12-30 | 45653.125 | 327.2779 | 0.69903 | 68.5503 | 4.7313 | 66.5817 | 10.0972 | 0 | 0 | 1348.8015 | 4.5911 | 4.6077 | 120.5595 | 120.4478 | 106.5148 | 117.2311 | 129.4782 | 130.0914 | 611.2132 | 723.4147 | 782.132 | 566.6893 | 0.3803
2024-12-30 | 45653.1667 | 330.9753 | 0.70813 | 70.6235 | 4.6583 | 68.2229 | 10.5376 | 0 | 0 | 1347.5625 | 4.4798 | 4.5414 | 120.6141 | 120.5754 | 106.4872 | 117.5444 | 129.8765 | 130.6527 | 608.567 | 728.485 | 782.3599 | 565.2175 | 1.045
2024-12-30 | 45653.2083 | 345.3071 | 0.70058 | 75.8411 | 4.6717 | 71.4572 | 10.1827 | 0 | 0 | 1351.5135 | 4.2225 | 4.3432 | 120.4536 | 120.4087 | 106.2613 | 119.5096 | 131.865 | 132.769 | 611.7846 | 747.1584 | 783.5569 | 567.9462 | 5.6008
2024-12-30 | 45653.25 | 411.5452 | 0.70572 | 101.6027 | 9.9253 | 92.2281 | 21.1579 | 17.2097 | 13.4868 | 1504.6311 | 3.8926 | 3.7871 | 126.4831 | 125.7361 | 110.1963 | 123.8559 | 136.837 | 137.3664 | 754.1539 | 899.3073 | 815.3152 | 689.3016 | 7.5862
2024-12-30 | 45653.2917 | 568.1257 | 0.66856 | 140.0453 | 21.3019 | 122.8138 | 22.423 | 24.1027 | 14.4408 | 1950.3685 | 3.6075 | 3.6176 | 137.4823 | 135.6228 | 116.8218 | 132.3086 | 147.4816 | 147.1327 | 1171.0084 | 1391.0292 | 1147.4392 | 802.9233 | 10.3145
2024-12-30 | 45653.3333 | 581.0013 | 0.65151 | 122.2357 | 31.3248 | 84.9071 | 17.918 | 25.4779 | 11.7927 | 1984.1815 | 3.907 | 3.8331 | 135.9188 | 134.497 | 114.9825 | 134.9953 | 149.9205 | 149.7115 | 1183.5609 | 1468.1309 | 1175.2354 | 808.9875 | 13.8493
2024-12-30 | 45653.375 | 585.2549 | 0.64882 | 121.4252 | 33.7139 | 83.4224 | 18.021 | 31.0404 | 14.489 | 1986.8379 | 3.9035 | 3.8286 | 134.5411 | 132.623 | 113.5708 | 134.5459 | 149.9638 | 149.7349 | 1165.9364 | 1474.8026 | 1180.6553 | 806.2241 | 18.8376
2024-12-30 | 45653.4167 | 585.6805 | 0.64457 | 124.0321 | 34.4355 | 85.2641 | 18.3379 | 31.0195 | 17.0251 | 1971.3674 | 3.8227 | 3.9165 | 133.4077 | 131.4286 | 112.4628 | 136.4189 | 151.5866 | 151.4442 | 1138.8832 | 1473.5773 | 1163.4973 | 807.8375 | 20.0156
2024-12-30 | 45653.4583 | 580.1604 | 0.65346 | 125.0151 | 27.7085 | 100.536 | 21.0734 | 31.0263 | 19.4034 | 1950.1759 | 3.8156 | 3.8403 | 134.0845 | 131.9535 | 113.2585 | 138.4695 | 153.355 | 153.2386 | 1119.6235 | 1463.5476 | 1151.3932 | 798.767 | 20.2512
2024-12-30 | 45653.5 | 579.155 | 0.64985 | 133.3545 | 23.6369 | 120.7294 | 27.861 | 33.4253 | 20.3933 | 1959.693 | 3.9534 | 3.8003 | 135.1089 | 132.7739 | 114.3218 | 139.7141 | 154.356 | 154.3398 | 1128.5374 | 1482.5774 | 1181.5187 | 778.1933 | 21.6988
2024-12-30 | 45653.5417 | 576.5562 | 0.65744 | 133.8553 | 15.9177 | 110.0114 | 21.2117 | 31.688 | 16.5354 | 1955.2444 | 3.9478 | 3.8445 | 134.9263 | 132.5795 | 114.3178 | 140.6042 | 154.9645 | 155.0159 | 1115.8534 | 1484.973 | 1178.6472 | 776.5919 | 22.5464
2024-12-30 | 45653.5833 | 573.2584 | 0.65278 | 121.053 | 9.9409 | 92.5099 | 14.2496 | 22.8027 | 8.7859 | 1945.7467 | 3.8993 | 3.9248 | 134.3991 | 132.2447 | 114.0176 | 140.8664 | 155.0237 | 155.1857 | 1100.8466 | 1477.3752 | 1168.1449 | 777.6293 | 22.4251
2024-12-30 | 45653.625 | 566.1596 | 0.65992 | 121.879 | 10.2701 | 87.8538 | 13.143 | 20.4942 | 11.2171 | 1929.4021 | 3.8475 | 3.8677 | 134.6233 | 132.7366 | 114.717 | 141.7276 | 155.1464 | 155.4551 | 1086.0117 | 1457.0757 | 1150.8495 | 778.5439 | 20.5389
2024-12-30 | 45653.6667 | 580.1719 | 0.65205 | 121.3492 | 10.2589 | 89.0517 | 10.3114 | 20.0877 | 13.1603 | 1974.8041 | 3.7823 | 3.8183 | 133.7547 | 131.37 | 113.5516 | 139.8299 | 153.9716 | 154.1041 | 1107.6859 | 1483.0074 | 1183.2423 | 791.5623 | 21.5365
2024-12-30 | 45653.7083 | 584.3797 | 0.64994 | 122.263 | 7.6927 | 89.9326 | 10.3762 | 20.6134 | 8.2817 | 1993.1948 | 3.8746 | 3.8732 | 133.2634 | 130.8801 | 112.9425 | 139.6144 | 154.0094 | 154.1367 | 1117.1407 | 1512.8691 | 1195.8098 | 797.3764 | 22.9723
2024-12-30 | 45653.75 | 584.7239 | 0.6534 | 124.5157 | 9.4838 | 89.856 | 11.3887 | 22.3264 | 12.0055 | 1991.2411 | 3.871 | 3.8358 | 132.4839 | 130.1151 | 112.1119 | 139.2019 | 153.7162 | 153.8544 | 1112.0035 | 1514.1575 | 1200.4943 | 790.762 | 22.5711
2024-12-30 | 45653.7917 | 589.7869 | 0.64767 | 127.3922 | 11.4546 | 97.6108 | 10.747 | 22.6693 | 18.2745 | 1998.4498 | 3.8643 | 3.9235 | 132.62 | 130.1522 | 111.9611 | 139.5587 | 154.0229 | 154.146 | 1124.9832 | 1536.28 | 1207.4788 | 790.9453 | 23.2027
2024-12-30 | 45653.8333 | 585.576 | 0.64789 | 126.8576 | 14.287 | 103.5626 | 11.3387 | 25.7871 | 20.2222 | 1985.2074 | 3.7296 | 3.9186 | 131.4043 | 129.0336 | 110.7952 | 139.7923 | 154.4513 | 154.5378 | 1115.3239 | 1530.8361 | 1190.7499 | 794.4465 | 22.6438
2024-12-30 | 45653.875 | 584.5872 | 0.64545 | 120.3841 | 13.0224 | 102.9171 | 10.9778 | 21.98 | 20.2611 | 1990.1617 | 3.7542 | 3.9559 | 130.7562 | 128.3784 | 110.007 | 138.6663 | 153.4573 | 153.5702 | 1123.9386 | 1538.2216 | 1191.0989 | 799.0684 | 21.9871
2024-12-30 | 45653.9167 | 579.6656 | 0.64289 | 110.8408 | 12.4139 | 96.2866 | 9.4031 | 16.0017 | 10.2083 | 1982.748 | 3.7057 | 3.982 | 130.1687 | 128.2411 | 109.4844 | 138.0311 | 152.2048 | 151.9387 | 1117.5638 | 1518.9963 | 1180.5896 | 802.1512 | 17.9808
2024-12-30 | 45653.9583 | 573.9703 | 0.63881 | 119.1123 | 11.4597 | 100.8611 | 10.348 | 17.5592 | 11.8805 | 1975.1082 | 3.7589 | 4.0215 | 128.6615 | 126.2686 | 108.3599 | 135.6846 | 150.2073 | 150.0349 | 1093.6791 | 1482.8737 | 1190.1982 | 784.9315 | 18.5889
2024-12-30 | 45654 | 552.1845 | 0.62774 | 111.0156 | 14.0264 | 91.5254 | 14.2284 | 19.629 | 14.4267 | 1918.308 | 3.8965 | 4.1049 | 127.0098 | 124.9438 | 107.2825 | 135.1539 | 149.5043 | 149.207 | 1036.6764 | 1409.1862 | 1143.4275 | 774.9142 | 19.428
2024-12-31 | 45654.0417 | 481.0524 | 0.63518 | 101.6501 | 8.7307 | 82.5375 | 18.798 | 21.9385 | 2.7867 | 1741.2181 | 4.7631 | 3.7993 | 125.0042 | 123.3809 | 106.5826 | 129.9994 | 143.8524 | 143.4056 | 900.9564 | 1193.3774 | 1072.4523 | 668.764 | 15.3454
2024-12-31 | 45654.0833 | 426.5804 | 0.64406 | 92.1822 | 7.4809 | 70.1544 | 15.2929 | 10.5952 | 5.2762 | 1630.5388 | 4.7641 | 4.0907 | 122.4729 | 121.1607 | 105.3889 | 126.4459 | 139.5994 | 139.1677 | 807.9368 | 1060.0229 | 998.6711 | 631.8507 | 10.4502
2024-12-31 | 45654.125 | 550.4219 | 0.65496 | 132.9042 | 11.8997 | 105.8884 | 10.638 | 18.5797 | 10.8493 | 1958.726 | 3.9469 | 3.8009 | 129.666 | 126.6194 | 109.1878 | 130.7836 | 145.1872 | 144.3378 | 1114.5397 | 1418.9067 | 1174.3633 | 784.3567 | 13.5241
2024-12-31 | 45654.1667 | 580.2249 | 0.62871 | 122.5483 | 18.0468 | 99.5408 | 20.1332 | 25.2723 | 17.5996 | 1986.8149 | 4.1841 | 4.0016 | 129.8572 | 127.2732 | 109.1928 | 135.7565 | 150.6649 | 149.9927 | 1130.0194 | 1501.0771 | 1207.7727 | 779.0219 | 20.4692
2024-12-31 | 45654.2083 | 532.3789 | 0.6445 | 111.5577 | 15.4264 | 88.8691 | 23.5121 | 16.5024 | 10.1405 | 1850.1162 | 4.0206 | 3.928 | 128.1574 | 126.1888 | 108.5713 | 133.9724 | 148.0931 | 147.6428 | 1006.275 | 1333.8723 | 1106.6595 | 743.496 | 16.7058
2024-12-31 | 45654.25 | 579.7941 | 0.63878 | 102.7746 | 19.6139 | 79.8181 | 15.863 | 15.0667 | 12.4737 | 1983.9268 | 3.8205 | 4.0138 | 130.3959 | 128.3116 | 109.752 | 136.4313 | 150.5652 | 149.9355 | 1131.488 | 1506.7338 | 1201.9821 | 781.9296 | 18.5982
2024-12-31 | 45654.2917 | 584.972 | 0.63941 | 104.9845 | 21.7561 | 92.9889 | 25.4856 | 26.4258 | 13.8078 | 1982.8456 | 3.8924 | 3.9673 | 128.8097 | 126.618 | 108.4051 | 136.2573 | 150.8102 | 150.2245 | 1110.5514 | 1507.0039 | 1198.6128 | 784.2351 | 22.1721
2024-12-31 | 45654.3333 | 587.2101 | 0.63752 | 111.2427 | 20.7068 | 96.7639 | 27.82 | 29.3148 | 11.8363 | 1982.0659 | 3.8736 | 3.8411 | 128.503 | 126.2039 | 107.8821 | 136.3879 | 151.0015 | 150.4265 | 1104.2428 | 1507.6438 | 1197.5293 | 784.5388 | 22.6462
2024-12-31 | 45654.375 | 585.9044 | 0.63679 | 119.0027 | 22.5551 | 96.085 | 25.5791 | 32.5134 | 14.5138 | 1986.1763 | 3.8823 | 3.7612 | 128.4031 | 126.0794 | 107.7617 | 136.7234 | 151.3663 | 150.6398 | 1102.7317 | 1516.7947 | 1202.1705 | 784.0048 | 24.3924
2024-12-31 | 45654.4167 | 583.0974 | 0.64094 | 119.8737 | 23.7413 | 95.6549 | 20.467 | 27.5299 | 15.0591 | 1980.1112 | 3.7539 | 3.9818 | 128.4456 | 126.1604 | 107.9241 | 137.8836 | 152.4036 | 151.7328 | 1092.1759 | 1517.7469 | 1201.123 | 778.9724 | 24.9213
2024-12-31 | 45654.4583 | 586.2944 | 0.63635 | 117.687 | 21.0352 | 89.2328 | 17.4336 | 27.2262 | 15.0421 | 1980.5374 | 3.8578 | 4.001 | 128.8308 | 126.577 | 108.4138 | 139.4522 | 153.825 | 152.9369 | 1092.7118 | 1534.0867 | 1204.8726 | 775.6798 | 25.8676
2024-12-31 | 45654.5 | 586.657 | 0.63535 | 121.4695 | 21.3163 | 92.8888 | 20.6866 | 30.3443 | 14.916 | 1961.8345 | 3.7894 | 3.9932 | 128.9549 | 126.6822 | 108.7364 | 140.504 | 154.7989 | 154.0556 | 1080.3217 | 1521.9828 | 1185.6643 | 776.1472 | 24.5519
2024-12-31 | 45654.5417 | 584.0872 | 0.6383 | 118.8681 | 21.4411 | 88.6261 | 19.4378 | 26.9822 | 15.451 | 1956.7241 | 3.6142 | 3.896 | 129.6322 | 127.5069 | 109.6384 | 141.4727 | 155.4306 | 154.7953 | 1071.4049 | 1510.2915 | 1165.0505 | 791.6951 | 23.9534
2024-12-31 | 45654.5833 | 579.9432 | 0.6416 | 115.2044 | 21.2067 | 88.8195 | 19.1338 | 27.1903 | 17.0974 | 1964.4663 | 3.8104 | 3.988 | 130.1054 | 128.0004 | 110.0683 | 141.858 | 155.9453 | 155.2689 | 1080.9012 | 1535.222 | 1172.1549 | 792.3298 | 25.5743
2024-12-31 | 45654.625 | 539.7997 | 0.6449 | 107.223 | 16.5175 | 79.8954 | 17.5425 | 27.8734 | 14.2354 | 1890.5786 | 4.1379 | 4.1067 | 128.4865 | 126.9853 | 109.2999 | 140.7952 | 154.7532 | 154.0049 | 1008.0787 | 1439.3053 | 1128.2246 | 762.3229 | 24.3116
2024-12-31 | 45654.6667 | 503.512 | 0.67187 | 109.2115 | 11.5358 | 86.4496 | 23.5602 | 23.4724 | 10.5214 | 1803.2014 | 4.1847 | 3.9684 | 125.9831 | 124.3097 | 107.5028 | 134.7735 | 148.0664 | 147.2964 | 935.6028 | 1274.6017 | 1072.6619 | 730.5757 | 17.605
2024-12-31 | 45654.7083 | 585.0618 | 0.6591 | 138.3747 | 15.8995 | 103.6497 | 4.8125 | 20.6997 | 18.5203 | 2013.4526 | 3.9948 | 4.0007 | 131.1596 | 128.8121 | 110.9055 | 140.0009 | 154.1456 | 153.0711 | 1130.2054 | 1550.4951 | 1221.3594 | 792.0829 | 23.4808
2024-12-31 | 45654.75 | 587.841 | 0.65702 | 121.4965 | 10.4086 | 113.4724 | 13.7652 | 26.4434 | 23.8908 | 1993.286 | 3.8796 | 3.9035 | 129.6202 | 127.3871 | 109.4544 | 142.4205 | 156.3944 | 155.7314 | 1111.4762 | 1557.7791 | 1205.0065 | 788.2756 | 25.0922
2024-12-31 | 45654.7917 | 578.1248 | 0.66268 | 98.7288 | 12.9525 | 83.6151 | 19.7234 | 22.8934 | 17.5265 | 1964.0137 | 3.8708 | 3.9583 | 129.2144 | 127.2874 | 109.1953 | 141.8782 | 155.8413 | 155.0739 | 1095.307 | 1531.3823 | 1175.5568 | 788.4815 | 23.068
2024-12-31 | 45654.8333 | 585.1021 | 0.6627 | 105.1115 | 11.014 | 91.9427 | 19.2589 | 24.1322 | 11.7647 | 1980.8009 | 3.8829 | 3.8588 | 129.6921 | 127.8472 | 109.4823 | 141.2849 | 154.9357 | 154.1931 | 1116.6393 | 1546.9871 | 1197.499 | 783.3043 | 22.9332
2024-12-31 | 45654.875 | 587.3254 | 0.66206 | 113.7092 | 14.0627 | 94.7674 | 15.4536 | 26.2025 | 17.4867 | 1990.5848 | 3.9063 | 3.5951 | 127.8632 | 125.6278 | 107.5182 | 140.2918 | 154.5392 | 153.4956 | 1115.1354 | 1558.8656 | 1208.0756 | 782.5044 | 24.939
2024-12-31 | 45654.9167 | 589.003 | 0.65871 | 113.9619 | 16.237 | 95.3034 | 11.8355 | 23.9787 | 17.7751 | 2045.4485 | 4.028 | 3.069 | 127.0363 | 124.6691 | 106.5538 | 139.9377 | 154.6383 | 153.2287 | 1151.9042 | 1623.5707 | 1263.6641 | 781.7794 | 27.8994
2024-12-31 | 45654.9583 | 568.7791 | 0.67167 | 117.8955 | 15.8631 | 97.2025 | 10.123 | 22.5413 | 16.9014 | 2062.9485 | 4.265 | 2.8715 | 123.7621 | 121.3733 | 103.5983 | 139.3489 | 153.9248 | 152.505 | 1146.429 | 1623.8584 | 1292.4198 | 770.5262 | 30.5173
2024-12-31 | 45655 | 538.4744 | 0.65319 | 108.5481 | 10.2176 | 79.8552 | 8.0743 | 22.0404 | 12.5662 | 1901.4738 | 4.3059 | 2.761 | 121.8459 | 119.9659 | 102.6229 | 138.9198 | 152.9668 | 151.6995 | 1024.7413 | 1450.7551 | 1176.7885 | 724.7199 | 28.3077
2025-01-01 | 45655.0417 | 499.5463 | 0.65624 | 109.3138 | 9.241 | 83.8237 | 14.0474 | 17.0841 | 9.878 | 1826.8805 | 4.5962 | 2.3019 | 121.5865 | 119.6494 | 102.7025 | 134.1781 | 147.8491 | 146.6149 | 970.9957 | 1304.3824 | 1106.7284 | 720.1545 | 21.7045
2025-01-01 | 45655.0833 | 330.5931 | 0.67682 | 67.6482 | 4.1066 | 60.1508 | 9.6021 | 2.7809 | 0 | 1375.4209 | 5.6377 | 2.7745 | 110.0953 | 109.703 | 96.0437 | 124.5502 | 136.4084 | 135.7839 | 594.4112 | 805.8146 | 814.248 | 561.1689 | 11.3199
2025-01-01 | 45655.125 | 325.2745 | 0.69676 | 63.0734 | 3.5584 | 62.6292 | 11.6322 | 11.7417 | 0 | 1352.0829 | 4.8971 | 2.3472 | 112.071 | 111.6401 | 97.797 | 119.9463 | 131.3729 | 131.1422 | 596.0936 | 751.5908 | 793.3868 | 558.7047 | 3.5838
2025-01-01 | 45655.1667 | 324.8316 | 0.6995 | 64.5926 | 2.933 | 62.4336 | 11.9508 | 13.272 | 3.9911 | 1388.6133 | 5.0072 | 2.4746 | 112.8164 | 113.0936 | 98.5548 | 118.4305 | 130.1027 | 130.0085 | 624.9528 | 772.9222 | 819.6227 | 568.9799 | 2.023
2025-01-01 | 45655.2083 | 438.7334 | 0.72343 | 109.7556 | 9.6764 | 92.0289 | 13.0476 | 20.3776 | 14.2472 | 1766.859 | 4.6874 | 2.4013 | 121.8754 | 119.9865 | 103.6641 | 123.2387 | 136.2017 | 135.3226 | 951.4135 | 1130.2531 | 1032.6823 | 734.1896 | 6.1618
2025-01-01 | 45655.25 | 527.7169 | 0.6691 | 117.1001 | 8.9244 | 90.8075 | 11.555 | 24.2613 | 12.6251 | 1942.052 | 4.7002 | 2.5204 | 126.3608 | 124.217 | 106.7328 | 130.6221 | 144.8443 | 143.3212 | 1098.7389 | 1364.8062 | 1178.9159 | 763.154 | 16.5502
2025-01-01 | 45655.2917 | 580.5385 | 0.66316 | 124.8995 | 6.1513 | 94.608 | 1.5429 | 10.9751 | 7.6839 | 2016.2643 | 3.9061 | 2.7256 | 127.7277 | 125.5413 | 107.3297 | 135.7779 | 150.3288 | 148.7258 | 1165.2972 | 1507.264 | 1229.9047 | 786.3373 | 21.166
2025-01-01 | 45655.3333 | 581.09 | 0.65746 | 116.766 | 8.684 | 94.2632 | 9.8598 | 20.6238 | 12.282 | 1950.2366 | 3.5811 | 2.9063 | 127.8323 | 126.2821 | 107.5194 | 138.6374 | 152.0424 | 151.1296 | 1114.4349 | 1459.0077 | 1166.4796 | 783.7908 | 18.3994
2025-01-01 | 45655.375 | 580.6825 | 0.66527 | 129.4209 | 11.4746 | 106.1911 | 15.3074 | 25.5043 | 16.1679 | 1909.0123 | 2.9479 | 2.9785 | 128.1223 | 126.2103 | 107.6034 | 138.236 | 152.3988 | 151.197 | 1084.1249 | 1413.2162 | 1117.2985 | 791.7123 | 17.2994
2025-01-01 | 45655.4167 | 585.2908 | 0.67163 | 131.1602 | 15.8344 | 111.0426 | 18.239 | 24.073 | 21.0462 | 1926.7517 | 2.5226 | 3.5335 | 128.5954 | 126.5648 | 107.9124 | 139.7102 | 154.1684 | 152.9745 | 1099.2344 | 1456.9042 | 1136.1145 | 790.6393 | 18.4282
2025-01-01 | 45655.4583 | 587.1711 | 0.67726 | 135.6039 | 13.7179 | 111.3129 | 15.0825 | 32.9733 | 26.8971 | 1935.6652 | 2.4123 | 3.6876 | 129.1811 | 127.0431 | 108.464 | 140.719 | 155.1358 | 154.0584 | 1107.9618 | 1481.528 | 1151.113 | 784.5644 | 20.6529
2025-01-01 | 45655.5 | 583.7999 | 0.67809 | 127.7509 | 14.1898 | 109.891 | 14.8256 | 33.049 | 27.2736 | 1944.126 | 2.354 | 3.7111 | 128.9693 | 127.0832 | 108.599 | 142.522 | 156.4929 | 155.8805 | 1102.4767 | 1504.9854 | 1162.1808 | 781.9581 | 25.6644
2025-01-01 | 45655.5417 | 567.2365 | 0.67932 | 124.3477 | 19.873 | 108.2238 | 22.4829 | 33.592 | 27.0973 | 1847.8789 | 2.7391 | 3.5036 | 128.9455 | 127.4949 | 109.1919 | 143.1072 | 156.8322 | 156.369 | 1025.2784 | 1387.5237 | 1064.0887 | 783.7981 | 19.3372
2025-01-01 | 45655.5833 | 566.2354 | 0.679 | 118.9151 | 12.8817 | 95.6039 | 9.7842 | 27.5285 | 23.5058 | 1891.9558 | 1.9983 | 3.6364 | 130.6189 | 128.9516 | 110.7577 | 141.9682 | 155.2125 | 154.533 | 1061.4619 | 1403.2698 | 1124.5643 | 767.38 | 13.8789
2025-01-01 | 45655.625 | 478.282 | 0.65191 | 87.3756 | 16.5788 | 73.9571 | 16.5217 | 13.7626 | 11.2713 | 1668.2485 | 4.0279 | 4.2265 | 125.9449 | 125.815 | 108.764 | 140.9297 | 152.9592 | 152.9729 | 852.8566 | 1167.2786 | 969.115 | 699.136 | 19.0589
2025-01-01 | 45655.6667 | 373.5963 | 0.68793 | 78.1084 | 9.2405 | 70.5558 | 12.4287 | 6.0548 | 5.2229 | 1423.4269 | 4.6806 | 4.5052 | 117.5754 | 117.2962 | 103.5513 | 129.6822 | 141.1621 | 140.9257 | 633.2873 | 835.9266 | 817.7451 | 605.6853 | 10.9097
2025-01-01 | 45655.7083 | 455.724 | 0.6938 | 111.0227 | 16.804 | 96.6017 | 15.2148 | 15.2706 | 13.2812 | 1637.9178 | 3.9509 | 3.8922 | 125.61 | 124.3714 | 108.7865 | 130.9522 | 143.1815 | 142.6177 | 828.7889 | 1031.7173 | 908.4379 | 729.4571 | 9.3015
2025-01-01 | 45655.75 | 573.8591 | 0.67137 | 129.9621 | 15.3814 | 108.3717 | 14.6639 | 15.8334 | 8.8294 | 1948.457 | 3.7231 | 3.7125 | 132.9733 | 131.0661 | 113.2679 | 137.4458 | 151.3789 | 150.4809 | 1116.3999 | 1407.4535 | 1144.736 | 803.7151 | 17.2051
2025-01-01 | 45655.7917 | 586.4054 | 0.65991 | 124.4819 | 13.334 | 107.2467 | 13.5884 | 17.2946 | 10.3486 | 1989.5177 | 3.6148 | 3.9452 | 130.5957 | 128.7865 | 110.8914 | 139.926 | 154.2099 | 153.3573 | 1133.8569 | 1493.3107 | 1193.2585 | 796.2859 | 21.6359
2025-01-01 | 45655.8333 | 580.7975 | 0.65876 | 110.6227 | 9.1043 | 91.8207 | 9.8183 | 14.3567 | 7.5197 | 1999.9923 | 3.9004 | 4.0218 | 128.7867 | 126.9353 | 108.8005 | 139.8867 | 154.2263 | 153.3481 | 1138.1169 | 1516.5879 | 1203.5065 | 796.5059 | 24.4855
2025-01-01 | 45655.875 | 571.9666 | 0.66781 | 114.0738 | 11.6827 | 95.6266 | 13.7026 | 15.6831 | 10.4406 | 1978.9038 | 3.8647 | 3.9149 | 128.1825 | 126.6235 | 108.1819 | 139.1034 | 153.1083 | 152.6563 | 1123.88 | 1490.1249 | 1177.6702 | 801.2365 | 23.465
2025-01-01 | 45655.9167 | 572.6669 | 0.66142 | 112.8327 | 11.8171 | 94.9554 | 11.326 | 16.7791 | 12.8608 | 1989.4034 | 3.9311 | 3.5988 | 126.4513 | 124.5779 | 106.3944 | 138.0784 | 152.7596 | 151.7665 | 1115.3309 | 1504.3508 | 1186.6781 | 802.7221 | 26.0588
2025-01-01 | 45655.9583 | 541.5642 | 0.6856 | 120.034 | 13.2085 | 97.8972 | 12.148 | 18.5727 | 13.6918 | 1900.915 | 3.8704 | 2.7901 | 124.2769 | 122.7413 | 104.754 | 136.744 | 150.9748 | 150.2039 | 1037.9209 | 1388.7063 | 1127.4214 | 773.4893 | 22.9388
2025-01-01 | 45656 | 496.0504 | 0.64319 | 102.3231 | 7.2618 | 84.3754 | 5.3109 | 12.8366 | 7.7475 | 1792.2052 | 4.5582 | 2.7029 | 121.2612 | 120.2577 | 103.0389 | 134.2768 | 148.267 | 147.327 | 950.3687 | 1282.4996 | 1112.0338 | 680.1536 | 23.5307
2025-01-02 | 45656.0417 | 324.1546 | 0.69914 | 62.111 | 5.4885 | 58.2671 | 7.9928 | 2.8229 | 0.71731 | 1357.9712 | 4.9552 | 2.4933 | 109.3197 | 110.1699 | 95.5115 | 122.3071 | 134.4235 | 134.6419 | 585.6548 | 772.8879 | 799.914 | 558.056 | 9.9111
2025-01-02 | 45656.0833 | 321.6751 | 0.70941 | 67.5168 | 3.9713 | 62.0786 | 7.723 | 5.5746 | 0 | 1387.6932 | 5.1471 | 2.8034 | 110.9307 | 111.2759 | 96.6396 | 116.8117 | 128.9606 | 129.0607 | 620.1534 | 772.3068 | 829.8426 | 557.8545 | 4.2232
2025-01-02 | 45656.125 | 321.962 | 0.71155 | 72.1901 | 0.79321 | 64.567 | 7.7188 | 5.4901 | 0 | 1415.1565 | 5.4599 | 1.7362 | 112.0293 | 111.7945 | 97.8034 | 115.815 | 128.3256 | 128.1193 | 646.8922 | 787.0118 | 857.9854 | 557.1897 | 2.4772
2025-01-02 | 45656.1667 | 325.0939 | 0.7042 | 78.6576 | 0.099412 | 66.8163 | 5.68 | 0.03241 | 0 | 1468.1752 | 5.7699 | 1.7304 | 112.7242 | 111.5959 | 98.1186 | 115.7518 | 128.3796 | 127.5753 | 691.837 | 831.3099 | 911.217 | 556.9671 | 2.8645
2025-01-02 | 45656.2083 | 323.6055 | 0.70777 | 75.277 | 0.66164 | 63.0466 | 6.6412 | 0 | 0 | 1488.9122 | 5.97 | 1.9105 | 112.0701 | 110.8938 | 97.3621 | 114.984 | 127.6472 | 126.1981 | 698.371 | 841.8544 | 931.1501 | 557.764 | 2.6823
2025-01-02 | 45656.25 | 438.8563 | 0.72989 | 120.6211 | 7.8423 | 106.5477 | 8.1258 | 19.7599 | 15.0706 | 1791.4454 | 4.7319 | 2.3923 | 121.5145 | 119.1655 | 103.3624 | 122.2166 | 135.5157 | 134.0739 | 980.0923 | 1150.9545 | 1047.2194 | 744.2405 | 6.288
2025-01-02 | 45656.2917 | 567.8695 | 0.67823 | 116.1329 | 6.4073 | 99.0303 | 2.7453 | 4.8999 | 0.40174 | 2097.9978 | 4.4638 | 1.816 | 128.4844 | 126.4866 | 108.2001 | 133.3415 | 148.1992 | 146.5336 | 1262.9326 | 1576.7872 | 1312.0085 | 786.0084 | 23.2612
2025-01-02 | 45656.3333 | 570.8544 | 0.68103 | 118.0502 | 8.0041 | 100.3354 | 7.2335 | 9.664 | 9.1249 | 2066.4519 | 4.2815 | 1.7942 | 124.8564 | 123.0011 | 104.782 | 138.7928 | 152.9415 | 152.0923 | 1216.5852 | 1576.576 | 1281.834 | 784.6586 | 29.1376
2025-01-02 | 45656.375 | 575.3117 | 0.68517 | 119.1186 | 7.4493 | 103.1365 | 13.0726 | 11.0042 | 5.6706 | 2074.5803 | 4.2753 | 2.0062 | 124.2664 | 121.428 | 103.9246 | 138.6954 | 153.7592 | 152.452 | 1215.6379 | 1602.0146 | 1294.2852 | 780.2965 | 33.9376
2025-01-02 | 45656.4167 | 575.4988 | 0.68356 | 123.6675 | 10.2856 | 104.8798 | 12.8417 | 11.0868 | 7.695 | 2041.2874 | 4.145 | 3.277 | 124.7503 | 122.1252 | 104.6897 | 141.5341 | 156.2903 | 155.247 | 1179.1548 | 1593.5233 | 1260.9645 | 780.3431 | 35.2688
2025-01-02 | 45656.4583 | 580.8926 | 0.681 | 127.2959 | 12.1785 | 108.0528 | 13.9733 | 14.0615 | 11.4431 | 2020.4312 | 3.9513 | 4.1042 | 125.3428 | 122.9078 | 105.4501 | 143.7637 | 158.1723 | 157.4549 | 1153.5364 | 1590.8607 | 1242.9808 | 777.4442 | 33.5749
2025-01-02 | 45656.5 | 580.1891 | 0.68368 | 129.0451 | 14.5656 | 107.6925 | 15.1658 | 14.6638 | 14.0183 | 1995.4832 | 3.6995 | 4.2089 | 125.3132 | 123.0882 | 105.7717 | 145.7603 | 159.8503 | 159.4561 | 1119.7336 | 1574.4102 | 1222.0339 | 773.4615 | 31.441
2025-01-02 | 45656.5417 | 565.1882 | 0.68136 | 115.7709 | 10.6376 | 93.3138 | 9.2835 | 8.9379 | 9.7335 | 1938.6443 | 3.6579 | 4.3625 | 125.6281 | 123.8395 | 106.4837 | 147.4811 | 160.8277 | 160.6648 | 1066.947 | 1512.8054 | 1171.3647 | 767.3286 | 27.7716
2025-01-02 | 45656.5833 | 569.9043 | 0.68378 | 135.158 | 10.0306 | 114.3737 | 9.6319 | 9.4123 | 10.3617 | 1929.9802 | 3.6579 | 4.0232 | 126.843 | 125.2892 | 107.7099 | 147.1118 | 159.7903 | 160.0307 | 1065.6376 | 1473.1198 | 1164.8442 | 765.144 | 22.1326
2025-01-02 | 45656.625 | 573.405 | 0.68039 | 131.3548 | 10.2511 | 116.8689 | 10.9955 | 15.2724 | 13.1973 | 1926.9469 | 3.6579 | 3.8744 | 127.0263 | 125.0414 | 107.6676 | 146.3576 | 159.4417 | 159.463 | 1062.156 | 1458.4128 | 1163.0349 | 763.92 | 21.3457
2025-01-02 | 45656.6667 | 553.5108 | 0.68576 | 133.9088 | 9.3032 | 114.5786 | 11.0289 | 21.9462 | 15.724 | 1842.4811 | 3.6579 | 3.4919 | 127.9125 | 126.1652 | 108.8973 | 146.5087 | 159.573 | 159.5699 | 1001.8912 | 1354.8356 | 1078.9097 | 763.552 | 16.865
2025-01-02 | 45656.7083 | 576.3634 | 0.68378 | 145.6749 | 7.4928 | 128.839 | 12.662 | 25.4564 | 17.5713 | 1913.7106 | 3.6617 | 3.505 | 130.7552 | 128.3713 | 110.7977 | 144.9368 | 158.4532 | 158.2151 | 1089.8595 | 1410.3051 | 1135.9893 | 777.7052 | 16.4446
2025-01-02 | 45656.75 | 590.4815 | 0.66177 | 128.6436 | 6.2011 | 117.3431 | 12.3005 | 26.9789 | 15.9134 | 1968.5247 | 4.3242 | 3.9461 | 130.5287 | 128.0958 | 110.4196 | 144.6924 | 158.6394 | 158.1503 | 1130.4224 | 1488.3528 | 1184.2688 | 784.2326 | 23.2028
2025-01-02 | 45656.7917 | 587.9314 | 0.66486 | 126.3261 | 6.0544 | 109.1814 | 9.4016 | 25.2776 | 15.5682 | 1950.0431 | 3.6681 | 3.9743 | 129.5708 | 127.1445 | 109.3529 | 145.0749 | 158.9094 | 158.5079 | 1116.4642 | 1474.0404 | 1174.0997 | 775.9161 | 20.9698
2025-01-02 | 45656.8333 | 582.6242 | 0.67067 | 110.8752 | 6.1084 | 89.0308 | 4.8812 | 19.6649 | 10.0537 | 1941.4314 | 3.5029 | 3.9624 | 129.6997 | 127.5229 | 109.2331 | 144.3354 | 157.7955 | 157.5953 | 1121.9027 | 1463.3893 | 1166.8705 | 774.5644 | 18.4421
2025-01-02 | 45656.875 | 585.8081 | 0.66721 | 120.3031 | 6.0767 | 99.9193 | 3.9184 | 19.8816 | 14.2199 | 1990.0472 | 3.838 | 4.1886 | 127.7181 | 125.276 | 107.2922 | 142.9868 | 156.8817 | 156.1377 | 1141.3147 | 1506.751 | 1216.0386 | 774.0349 | 22.0316
2025-01-02 | 45656.9167 | 585.264 | 0.67389 | 125.2521 | 5.8497 | 109.2803 | 3.5474 | 21.5487 | 15.7816 | 1971.1157 | 3.6796 | 4.1431 | 126.7454 | 124.1517 | 106.1946 | 142.5154 | 156.7183 | 155.9523 | 1124.5676 | 1487.8508 | 1199.5217 | 771.5927 | 21.6892
2025-01-02 | 45656.9583 | 482.0549 | 0.66533 | 103.6672 | 5.9392 | 87.2603 | 3.2846 | 20.7723 | 14.9211 | 1684.0538 | 5.046 | 4.5084 | 121.3329 | 120.1463 | 103.3371 | 139.2256 | 152.4826 | 152.2404 | 872.617 | 1166.1475 | 1003.0975 | 680.92 | 20.3581
2025-01-02 | 45657 | 489.7566 | 0.70092 | 110.2761 | 8.7836 | 94.1879 | 17.5734 | 22.2362 | 12.6807 | 1737.7728 | 4.7804 | 3.8676 | 123.3594 | 121.3252 | 104.4047 | 132.1429 | 145.7151 | 145.2706 | 944.0582 | 1162.4991 | 1023.2007 | 714.5667 | 13.2059
2025-01-03 | 45657.0417 | 535.3169 | 0.6725 | 114.6547 | 6.2748 | 93.3264 | 5.7289 | 21.9804 | 9.7335 | 1870.8701 | 4.7216 | 4.0884 | 128.2644 | 126.3344 | 108.0018 | 137.5049 | 151.1775 | 150.8422 | 1086.7817 | 1346.9393 | 1098.8207 | 772.075 | 16.3795
2025-01-03 | 45657.0833 | 436.5445 | 0.67921 | 103.1731 | 4.7512 | 76.3513 | 9.0191 | 5.2691 | 2.8935 | 1579.8207 | 5.1508 | 4.3045 | 120.5061 | 120.2142 | 103.6092 | 133.866 | 146.3671 | 146.3013 | 808.3004 | 1034.5454 | 939.6896 | 640.1494 | 13.9758
2025-01-03 | 45657.125 | 394.6341 | 0.70437 | 93.8952 | 7.0417 | 72.1045 | 8.8113 | 9.523 | 5.9134 | 1459.9766 | 5.3492 | 3.4052 | 116.4668 | 115.4235 | 100.7912 | 126.7667 | 139.4386 | 139.3931 | 711.5978 | 879.9446 | 883.4114 | 576.5516 | 9.3647
2025-01-03 | 45657.1667 | 339.2994 | 0.70674 | 77.8861 | 4.3141 | 70.2653 | 6.446 | 8.7264 | 0 | 1376.389 | 6.0558 | 2.7123 | 115.0335 | 114.6701 | 100.4196 | 122.6556 | 135.129 | 135.0899 | 640.9223 | 782.8742 | 808.1616 | 568.222 | 7.6935
2025-01-03 | 45657.2083 | 314.3562 | 0.74602 | 74.6258 | 0.65 | 73.7074 | 5.9684 | 9.264 | 1.5783 | 1344.1002 | 5.9749 | 2.0494 | 112.3474 | 113.2304 | 98.4804 | 116.1593 | 128.6255 | 128.7581 | 604.3538 | 722.4419 | 782.5518 | 561.5748 | 3.2205
2025-01-03 | 45657.25 | 330.5381 | 0.75314 | 79.9916 | 0.73305 | 80.8217 | 13.5783 | 17.1105 | 6.5558 | 1381.9698 | 5.7026 | 1.7732 | 113.6521 | 114.1769 | 99.2812 | 115.4956 | 127.9871 | 127.9984 | 632.9102 | 742.0734 | 791.7438 | 590.2138 | 0.82126
2025-01-03 | 45657.2917 | 517.8664 | 0.71788 | 142.9426 | 9.6286 | 128.8402 | 11.5547 | 18.4609 | 18.6125 | 1902.853 | 4.9457 | 1.3705 | 128.9799 | 127.1402 | 108.857 | 126.9472 | 141.5488 | 140.2851 | 1128.2771 | 1307.5524 | 1089.8038 | 813.0527 | 11.2362
2025-01-03 | 45657.3333 | 576.3207 | 0.69641 | 151.0636 | 17.331 | 120.3156 | 6.5385 | 23.1168 | 27.3351 | 2020.4595 | 4.4787 | 1.5499 | 129.4839 | 127.7682 | 108.7806 | 135.203 | 150.5828 | 149.1366 | 1211.5219 | 1530.7577 | 1223.9769 | 796.5195 | 23.9972
2025-01-03 | 45657.375 | 585.1656 | 0.70172 | 148.9946 | 18.2066 | 119.8599 | 7.9305 | 27.4517 | 29.0458 | 2010.6115 | 3.7116 | 1.593 | 128.2006 | 126.2177 | 107.4177 | 138.8651 | 154.1258 | 152.8175 | 1182.9856 | 1560.6609 | 1224.3544 | 786.2566 | 26.6661
2025-01-03 | 45657.4167 | 588.5852 | 0.69751 | 143.7911 | 17.0394 | 113.2506 | 6.319 | 25.6222 | 29.522 | 2015.2668 | 3.1468 | 2.8966 | 127.8934 | 125.6729 | 107.0953 | 139.8361 | 155.0889 | 153.9457 | 1175.9369 | 1576.3866 | 1229.3751 | 785.876 | 27.585
2025-01-03 | 45657.4583 | 584.8457 | 0.70087 | 122.5535 | 13.5479 | 101.9733 | 12.2763 | 25.9336 | 25.6826 | 1971.415 | 2.3141 | 4.5201 | 128.1392 | 126.2995 | 107.4915 | 141.0666 | 155.8299 | 155.0409 | 1139.9324 | 1532.0371 | 1185.0923 | 786.3295 | 22.8652
2025-01-03 | 45657.5 | 582.0984 | 0.69907 | 127.5929 | 14.2821 | 107.9794 | 14.0097 | 28.5079 | 27.0279 | 1954.9784 | 1.9663 | 5.4326 | 129.2443 | 127.4949 | 108.9288 | 141.9212 | 156.148 | 155.6136 | 1112.9335 | 1495.051 | 1169.5067 | 785.4471 | 25.9918
2025-01-03 | 45657.5417 | 576.4897 | 0.69825 | 126.9349 | 13.7249 | 108.8722 | 15.8664 | 32.457 | 26.2118 | 1942.0083 | 2.8147 | 4.0425 | 129.2793 | 127.2866 | 109.0681 | 141.8806 | 156.0258 | 155.4572 | 1094.3472 | 1469.472 | 1168.2255 | 773.756 | 25.3909
2025-01-03 | 45657.5833 | 578.0152 | 0.69034 | 127.6035 | 14.5414 | 109.2834 | 15.6247 | 32.7914 | 28.2703 | 1941.8523 | 2.2825 | 4.0131 | 131.4915 | 129.3441 | 111.3808 | 142.6821 | 156.9076 | 155.9539 | 1097.9539 | 1452.3987 | 1168.6281 | 773.1911 | 19.8216
2025-01-03 | 45657.625 | 578.7921 | 0.67924 | 123.2906 | 14.2726 | 106.101 | 17.2719 | 33.3954 | 29.1801 | 1947.3959 | 2.6047 | 3.895 | 133.1199 | 130.9299 | 112.9206 | 143.5904 | 157.5537 | 156.8838 | 1108.0448 | 1465.4103 | 1171.1864 | 776.1672 | 20.1311
2025-01-03 | 45657.6667 | 531.7621 | 0.68338 | 117.9626 | 11.1255 | 97.7381 | 13.9191 | 25.1692 | 22.3506 | 1836.78 | 5.2217 | 4.2423 | 130.2928 | 128.8607 | 111.3172 | 141.7505 | 155.1509 | 154.7366 | 1005.7852 | 1311.5107 | 1069.027 | 767.7602 | 20.4949
2025-01-03 | 45657.7083 | 587.0345 | 0.67654 | 141.2325 | 6.4554 | 124.3175 | 4.9687 | 34.8206 | 27.2953 | 1962.4373 | 4.0488 | 3.8843 | 135.2777 | 132.968 | 114.6832 | 141.3774 | 155.417 | 154.8019 | 1156.7493 | 1460.9287 | 1167.4939 | 794.945 | 19.6823
2025-01-03 | 45657.75 | 585.4354 | 0.67868 | 138.5061 | 6.4554 | 115.5303 | 5.3181 | 33.5714 | 23.8598 | 1957.5854 | 3.236 | 4.0137 | 133.3983 | 131.2993 | 112.9909 | 142.262 | 156.3106 | 155.6511 | 1129.5422 | 1459.8818 | 1174.5129 | 783.0788 | 19.0827
2025-01-03 | 45657.7917 | 589.0314 | 0.67422 | 135.5927 | 6.5608 | 118.1926 | 6.7218 | 36.0814 | 29.1537 | 1969.105 | 3.8018 | 4.0355 | 132.6121 | 130.3613 | 112.1515 | 140.6285 | 154.8652 | 154.0764 | 1135.0869 | 1465.0009 | 1196.799 | 772.3284 | 19.9994
2025-01-03 | 45657.8333 | 584.1541 | 0.67899 | 133.3403 | 7.7706 | 114.9084 | 5.2746 | 34.623 | 28.3486 | 1957.4773 | 3.3393 | 4.1039 | 131.4276 | 129.0821 | 111.0641 | 140.4552 | 154.6154 | 153.9261 | 1121.3817 | 1453.6177 | 1190.0814 | 767.3712 | 18.6057
2025-01-03 | 45657.875 | 580.2881 | 0.68401 | 119.8017 | 8.1465 | 96.7015 | 5.8245 | 28.901 | 24.5744 | 1950.8359 | 2.7697 | 4.1045 | 131.2002 | 129.0221 | 110.8428 | 139.352 | 153.3682 | 152.5737 | 1122.4108 | 1439.8627 | 1184.7969 | 766.0295 | 15.2975
2025-01-03 | 45657.9167 | 577.1465 | 0.67742 | 123.1593 | 10.8599 | 105.1524 | 9.1248 | 32.4284 | 29.7929 | 1943.059 | 2.6184 | 4.1492 | 131.6058 | 129.4881 | 111.1376 | 139.5125 | 153.3314 | 152.8824 | 1126.8473 | 1433.2837 | 1156.4536 | 786.6237 | 15.3436
2025-01-03 | 45657.9583 | 531.8395 | 0.68591 | 118.3908 | 10.1721 | 108.5335 | 9.9897 | 25.494 | 26.2342 | 1867.1056 | 4.372 | 4.505 | 127.4918 | 125.6162 | 107.9365 | 137.5897 | 151.3183 | 150.6065 | 1031.4286 | 1325.3304 | 1093.8451 | 773.2787 | 18.7325
2025-01-03 | 45658 | 574.3121 | 0.68126 | 131.325 | 6.4021 | 114.6856 | 4.9785 | 25.6777 | 24.512 | 1970.7346 | 3.6753 | 4.3556 | 129.9762 | 127.4413 | 109.1859 | 138.9712 | 153.5018 | 152.4581 | 1141.9229 | 1479.8348 | 1171.1073 | 799.63 | 20.3673
2025-01-04 | 45658.0417 | 541.816 | 0.67968 | 120.4643 | 5.9575 | 106.412 | 5.4653 | 27.102 | 25.0833 | 1871.3691 | 4.8126 | 4.3879 | 127.5512 | 125.6124 | 107.6208 | 138.5382 | 152.9292 | 152.1157 | 1044.8251 | 1368.1874 | 1085.9185 | 785.4625 | 23.3225
2025-01-04 | 45658.0833 | 514.8569 | 0.66652 | 111.4772 | 5.8293 | 98.7693 | 6.2131 | 19.0815 | 17.0663 | 1812.5305 | 5.2541 | 3.1739 | 125.2623 | 123.6574 | 105.9237 | 135.2102 | 149.425 | 148.6985 | 985.2653 | 1274.1855 | 1056.3403 | 756.1606 | 21.7798
2025-01-04 | 45658.125 | 369.872 | 0.66765 | 69.3898 | 4.7222 | 63.2613 | 4.5725 | 0 | 0 | 1428.595 | 6.869 | 2.5575 | 116.2408 | 116.3794 | 101.1553 | 124.8604 | 137.7894 | 137.3716 | 664.45 | 847.5176 | 832.6186 | 595.9604 | 13.3381
2025-01-04 | 45658.1667 | 346.6525 | 0.71319 | 75.4503 | 5.1144 | 65.8273 | 4.2061 | 6.7721 | 5.6409 | 1413.0521 | 6.8346 | 2.017 | 113.8212 | 112.7367 | 99.0061 | 116.7008 | 129.2642 | 128.5023 | 648.7438 | 775.439 | 806.4594 | 606.5848 | 4.9882
2025-01-04 | 45658.2083 | 421.0511 | 0.7016 | 106.3427 | 10.2044 | 83.79 | 9.5726 | 4.2413 | 12.1689 | 1586.8943 | 5.6394 | 1.8428 | 121.7791 | 120.49 | 104.5414 | 121.3673 | 134.6479 | 133.669 | 817.8273 | 956.3305 | 905.318 | 681.5938 | 5.7576
2025-01-04 | 45658.25 | 490.8759 | 0.6923 | 127.162 | 7.9388 | 106.4937 | 10.507 | 12.9567 | 8.4107 | 1760.0426 | 5.2971 | 2.5181 | 127.286 | 125.5881 | 108.0382 | 125.9352 | 139.9564 | 138.9659 | 995.0289 | 1156.4302 | 1034.5293 | 725.4991 | 9.3788
2025-01-04 | 45658.2917 | 571.6555 | 0.69105 | 137.5206 | 6.6099 | 116.2965 | 4.271 | 16.3482 | 13.0817 | 1973.515 | 4.4147 | 3.265 | 132.7698 | 130.9736 | 111.6133 | 134.5712 | 148.8986 | 148.4103 | 1201.6938 | 1453.8547 | 1178.5197 | 795.0003 | 13.7289
2025-01-04 | 45658.3333 | 587.086 | 0.68261 | 133.9241 | 7.8176 | 110.2739 | 6.7446 | 18.6661 | 15.8286 | 1988.2955 | 3.7474 | 3.9216 | 130.1847 | 128.3151 | 109.287 | 137.5387 | 152.2818 | 151.4564 | 1180.9742 | 1508.3857 | 1210.6431 | 777.639 | 21.4668
2025-01-04 | 45658.375 | 589.1616 | 0.68134 | 134.6233 | 8.7522 | 108.3124 | 11.2832 | 23.4849 | 15.8477 | 1944.132 | 2.5855 | 3.433 | 129.7793 | 127.6113 | 108.8891 | 138.5506 | 153.2681 | 152.3904 | 1136.7614 | 1460.4321 | 1165.5674 | 778.5118 | 18.9402
2025-01-04 | 45658.4167 | 585.9418 | 0.69545 | 142.4594 | 13.2728 | 119.5701 | 15.5579 | 29.9397 | 21.7745 | 1897.8896 | 1.8556 | 3.199 | 131.5982 | 129.688 | 110.8252 | 139.2107 | 153.8325 | 153.2178 | 1110.8514 | 1398.5504 | 1114.0789 | 783.797 | 14.8464
2025-01-04 | 45658.4583 | 591.6616 | 0.69644 | 137.7292 | 16.3754 | 112.3443 | 17.5088 | 32.1116 | 28.0631 | 1946.0264 | 1.4648 | 3.6498 | 132.417 | 130.2843 | 111.4385 | 139.4417 | 154.1476 | 153.4686 | 1146.8577 | 1450.1606 | 1155.1963 | 790.8107 | 13.8664
2025-01-04 | 45658.5 | 595.3715 | 0.69702 | 142.993 | 17.9735 | 118.1247 | 17.4785 | 39.265 | 37.0405 | 1978.7109 | 1.249 | 3.7085 | 134.4999 | 132.0698 | 113.1719 | 141.2631 | 156.2058 | 155.3414 | 1181.8146 | 1497.7207 | 1194.0774 | 784.6388 | 17.4856
2025-01-04 | 45658.5417 | 592.5233 | 0.69063 | 123.3802 | 10.6055 | 98.3524 | 11.0423 | 32.0777 | 26.179 | 1947.451 | 1.7135 | 3.6742 | 132.8679 | 130.954 | 112.4391 | 141.9574 | 156.4454 | 155.8277 | 1141.5173 | 1463.7096 | 1159.5018 | 787.9622 | 13.882
2025-01-04 | 45658.5833 | 581.387 | 0.67748 | 118.9716 | 9.9012 | 96.5803 | 10.6485 | 28.6023 | 27.8878 | 1940.4106 | 2.104 | 3.9132 | 132.38 | 130.7946 | 112.2135 | 142.2495 | 156.0501 | 155.8819 | 1123.4392 | 1446.6746 | 1160.5674 | 779.8559 | 11.5433
2025-01-04 | 45658.625 | 581.7145 | 0.67059 | 118.9322 | 6.969 | 101.1248 | 4.189 | 26.8707 | 22.6717 | 1939.5171 | 1.9912 | 3.975 | 131.2914 | 129.2626 | 111.2656 | 141.6956 | 155.5567 | 154.9153 | 1106.5354 | 1439.6094 | 1178.5186 | 760.9989 | 11.7368
2025-01-04 | 45658.6667 | 584.8541 | 0.6667 | 128.3152 | 9.415 | 103.2172 | 7.4868 | 29.9109 | 23.1703 | 1903.0245 | 1.5939 | 3.4281 | 132.0992 | 130.1451 | 112.1192 | 141.6127 | 155.3501 | 154.6983 | 1087.5059 | 1389.1515 | 1138.3101 | 764.7056 | 8.7119
2025-01-04 | 45658.7083 | 586.5976 | 0.66549 | 127.8236 | 10.0384 | 110.6681 | 11.7365 | 32.016 | 25.746 | 1906.1901 | 1.555 | 3.3578 | 132.9013 | 130.9451 | 112.8749 | 140.3896 | 154.3167 | 153.6988 | 1093.9391 | 1372.6697 | 1134.9907 | 771.2063 | 7.5705
2025-01-04 | 45658.75 | 590.4291 | 0.6603 | 127.3533 | 12.8869 | 109.8055 | 12.0098 | 35.8277 | 27.3139 | 1922.7261 | 1.9747 | 3.5052 | 133.3958 | 131.4367 | 113.2826 | 140.0419 | 154.1461 | 153.3288 | 1103.645 | 1387.8754 | 1146.5186 | 776.1942 | 9.4902
2025-01-04 | 45658.7917 | 587.135 | 0.66333 | 111.6208 | 7.684 | 100.0937 | 12.6741 | 33.2363 | 23.4626 | 1916.3394 | 2.3342 | 3.71 | 132.6199 | 130.6861 | 112.3678 | 140.3217 | 154.3873 | 153.6157 | 1101.4091 | 1387.8561 | 1131.625 | 784.7295 | 9.5878
2025-01-04 | 45658.8333 | 579.9467 | 0.67974 | 120.8652 | 11.675 | 105.4028 | 20.2057 | 37.4369 | 25.7392 | 1895.9027 | 1.8787 | 3.5149 | 133.1453 | 131.6768 | 112.9244 | 140.4069 | 153.8689 | 153.6975 | 1099.1031 | 1366.5525 | 1110.2864 | 785.5883 | 7.4182
2025-01-04 | 45658.875 | 582.7797 | 0.67799 | 128.3854 | 11.9589 | 112.5369 | 15.9528 | 39.6487 | 28.6557 | 1913.2247 | 1.5297 | 3.6176 | 133.0827 | 131.0789 | 112.6271 | 139.3434 | 153.5332 | 152.9357 | 1112.8046 | 1383.0475 | 1125.0398 | 788.1365 | 8.8314
2025-01-04 | 45658.9167 | 589.5969 | 0.67475 | 122.5384 | 9.9591 | 112.3809 | 12.5055 | 38.2908 | 25.8593 | 1994.5587 | 4.7109 | 4.0586 | 132.4394 | 130.2193 | 111.6125 | 139.0426 | 153.8515 | 152.812 | 1170.1075 | 1488.6331 | 1205.2277 | 789.3578 | 14.6525
2025-01-04 | 45658.9583 | 589.7609 | 0.67746 | 121.7306 | 9.9661 | 111.6969 | 11.771 | 36.7839 | 29.4712 | 2004.7537 | 4.12 | 4.2189 | 130.7614 | 128.328 | 109.9358 | 140.3005 | 155.2259 | 154.1077 | 1168.6169 | 1515.5764 | 1215.7977 | 788.9683 | 15.9468
2025-01-04 | 45659 | 588.2792 | 0.67163 | 123.0098 | 9.3565 | 105.4558 | 14.263 | 37.521 | 26.7588 | 2001.1483 | 5.0431 | 4.1177 | 129.7686 | 127.3857 | 109.0701 | 140.1161 | 154.8738 | 153.7411 | 1155.1409 | 1504.8123 | 1210.0432 | 791.108 | 17.5379
2025-01-05 | 45659.0417 | 541.4312 | 0.68207 | 126.9482 | 13.0652 | 99.9653 | 16.5001 | 34.761 | 27.6849 | 1845.5651 | 5.2162 | 3.9688 | 126.6742 | 125.2208 | 107.1961 | 137.7805 | 151.9061 | 151.0412 | 1010.0233 | 1300.6681 | 1062.8151 | 782.7645 | 13.8672
2025-01-05 | 45659.0833 | 555.5776 | 0.69304 | 137.7666 | 11.9516 | 108.5992 | 15.6934 | 35.4893 | 29.5328 | 1899.9683 | 4.7201 | 3.8607 | 127.5049 | 125.5804 | 107.54 | 136.2428 | 150.4231 | 149.5584 | 1064.7191 | 1342.7327 | 1122.0427 | 777.9111 | 11.9699
2025-01-05 | 45659.125 | 566.5778 | 0.67677 | 120.1125 | 10.2495 | 94.8691 | 13.6152 | 38.7222 | 25.716 | 1967.2343 | 5.8215 | 4.1738 | 127.7876 | 125.6894 | 107.3797 | 136.932 | 151.7626 | 150.4952 | 1122.1989 | 1441.1726 | 1193.7769 | 773.4479 | 16.3267
2025-01-05 | 45659.1667 | 489.9047 | 0.70199 | 110.5203 | 8.7335 | 89.2779 | 10.7327 | 26.7799 | 22.2182 | 1746.5303 | 6.7573 | 4.2219 | 124.2762 | 123.5347 | 105.6115 | 135.0086 | 148.1956 | 148.0562 | 937.4164 | 1203.7833 | 1010.7357 | 735.7891 | 13.1548
2025-01-05 | 45659.2083 | 554.2486 | 0.68363 | 135.3311 | 12.9053 | 106.2312 | 8.5025 | 35.113 | 29.7768 | 1902.5045 | 4.5276 | 3.6847 | 126.4486 | 124.5274 | 106.4203 | 135.6708 | 149.9907 | 149.0363 | 1075.4688 | 1367.9971 | 1112.2451 | 790.2744 | 12.2424
2025-01-05 | 45659.25 | 575.2169 | 0.67718 | 128.4252 | 14.2736 | 105.6644 | 8.2299 | 36.8327 | 27.1544 | 1951.4047 | 3.2648 | 3.5226 | 127.147 | 124.9708 | 106.678 | 136.635 | 151.3333 | 150.2881 | 1119.6545 | 1435.1788 | 1162.7085 | 788.6747 | 12.7536
2025-01-05 | 45659.2917 | 583.7562 | 0.67173 | 122.5814 | 10.5109 | 113.6848 | 11.9593 | 39.2631 | 27.1197 | 1968.021 | 4.1584 | 3.4178 | 128.4255 | 126.1249 | 107.6481 | 137.1347 | 151.9912 | 151.0144 | 1146.1429 | 1463.1676 | 1178.377 | 789.6292 | 15.0824
2025-01-05 | 45659.3333 | 586.1324 | 0.67795 | 128.9849 | 9.2682 | 114.3021 | 13.4422 | 31.0771 | 23.3412 | 1975.5968 | 1.9667 | 3.9785 | 127.3972 | 125.1994 | 106.8402 | 137.6419 | 152.4973 | 151.4695 | 1136.3403 | 1470.1025 | 1190.9072 | 784.7087 | 13.1452
2025-01-05 | 45659.375 | 590.6134 | 0.67579 | 120.1612 | 8.4753 | 112.4304 | 9.6672 | 31.5664 | 25.3246 | 2002.4066 | 4.5612 | 3.8034 | 127.4334 | 124.9713 | 106.6813 | 137.2458 | 152.1781 | 151.0738 | 1162.5332 | 1489.5967 | 1220.6516 | 781.7332 | 18.8029
2025-01-05 | 45659.4167 | 588.9911 | 0.679 | 127.3288 | 5.9747 | 110.5945 | 9.0811 | 32.1945 | 22.9238 | 1983.903 | 4.0814 | 3.7336 | 127.7909 | 125.3483 | 107.1396 | 137.088 | 151.9583 | 150.9759 | 1149.0322 | 1469.7762 | 1206.3016 | 777.6189 | 18.5524
2025-01-05 | 45659.4583 | 586.9903 | 0.67788 | 119.3549 | 5.9747 | 95.4705 | 7.7232 | 27.1503 | 22.4175 | 1983.5646 | 2.9953 | 3.9296 | 128.102 | 125.6207 | 107.4486 | 138.2926 | 152.9877 | 151.9092 | 1144.5973 | 1480.9888 | 1208.9994 | 774.5585 | 16.8482
2025-01-05 | 45659.5 | 580.8694 | 0.6867 | 119.2552 | 6.1222 | 96.0042 | 5.2865 | 27.0574 | 21.405 | 1968.6296 | 1.7691 | 3.931 | 130.4162 | 128.3969 | 109.9675 | 140.7006 | 154.5879 | 153.9504 | 1147.1825 | 1480.3182 | 1190.4484 | 778.1422 | 14.8213
2025-01-05 | 45659.5417 | 581.7853 | 0.68784 | 122.8814 | 6.0167 | 106.4508 | 3.812 | 23.4997 | 22.1983 | 2000.9741 | 2.5304 | 4.202 | 129.2097 | 126.8123 | 108.9968 | 142.0765 | 156.1885 | 155.0968 | 1145.713 | 1518.3649 | 1231.9401 | 769.0002 | 20.4175
2025-01-05 | 45659.5833 | 576.9855 | 0.68837 | 126.8175 | 5.7775 | 105.2586 | 1.1614 | 25.8041 | 23.3712 | 1984.8667 | 2.2183 | 4.1309 | 129.1018 | 126.8077 | 109.2545 | 144.8118 | 158.6016 | 157.6406 | 1117.4351 | 1514.7764 | 1212.4719 | 772.3975 | 20.5821
2025-01-05 | 45659.625 | 557.2076 | 0.6748 | 122.1172 | 6.3054 | 103.9297 | 2.3691 | 27.8656 | 28.1145 | 1920.0729 | 3.5999 | 4.1389 | 129.407 | 127.3887 | 109.9866 | 145.7795 | 159.2242 | 158.4431 | 1061.7173 | 1431.7646 | 1152.5909 | 767.4886 | 18.39
2025-01-05 | 45659.6667 | 456.3329 | 0.6916 | 92.9299 | 5.1147 | 67.3544 | 3.4241 | 8.5823 | 3.8072 | 1623.9475 | 7.0691 | 4.1656 | 123.4854 | 122.9403 | 106.8832 | 138.6944 | 150.9216 | 150.6275 | 806.8011 | 1063.8639 | 956.9471 | 666.9841 | 13.7278
2025-01-05 | 45659.7083 | 525.3543 | 0.71204 | 119.8949 | 15.3738 | 102.2282 | 20.8092 | 25.801 | 16.8009 | 1806.3439 | 4.1734 | 3.3757 | 129.7672 | 127.9697 | 111.0905 | 136.5628 | 149.5949 | 149.0264 | 983.9109 | 1210.4932 | 1043.7322 | 762.6121 | 7.5662
2025-01-05 | 45659.75 | 590.0287 | 0.69552 | 145.3689 | 8.8824 | 117.5832 | 11.4095 | 32.049 | 26.8722 | 2040.4581 | 1.7646 | 3.3586 | 132.6652 | 130.7201 | 112.8731 | 142.393 | 156.278 | 155.6033 | 1125.9285 | 1445.3989 | 1182.0656 | 858.3681 | 12.1019
2025-01-05 | 45659.7917 | 589.7598 | 0.6857 | 121.6113 | 9.5816 | 96.7374 | 13.0109 | 30.7568 | 20.4028 | 2008.887 | 3.5425 | 3.7451 | 132.3604 | 130.2726 | 112.2992 | 143.4434 | 157.3464 | 156.6255 | 1145.2552 | 1472.9955 | 1206.1346 | 802.7576 | 13.5242
2025-01-05 | 45659.8333 | 591.6379 | 0.68392 | 121.0381 | 8.2502 | 98.847 | 12.4035 | 31.8245 | 21.6017 | 1981.9984 | 2.6317 | 3.7605 | 132.2204 | 130.4161 | 112.2149 | 143.019 | 156.7468 | 156.2172 | 1155.5391 | 1481.2078 | 1214.2069 | 767.808 | 10.5518
2025-01-05 | 45659.875 | 598.5441 | 0.67259 | 120.7091 | 11.5001 | 95.788 | 14.1668 | 33.1597 | 28.6413 | 1989.4509 | 2.1293 | 3.7678 | 131.479 | 129.248 | 111.0253 | 141.2098 | 155.5362 | 154.673 | 1162.0034 | 1483.4659 | 1220.3152 | 769.1151 | 11.3656
2025-01-05 | 45659.9167 | 581.7899 | 0.67749 | 123.3915 | 11.6539 | 105.2253 | 18.8361 | 35.1064 | 26.0684 | 1983.0566 | 3.4837 | 3.7217 | 130.0638 | 127.9613 | 109.7489 | 140.3428 | 154.6247 | 153.6492 | 1146.392 | 1459.7816 | 1212.1567 | 770.8892 | 13.7401
2025-01-05 | 45659.9583 | 540.2938 | 0.64978 | 116.0527 | 8.4097 | 95.6338 | 11.4362 | 34.7898 | 24.6522 | 1851.292 | 4.7754 | 4.157 | 127.3551 | 125.9235 | 107.9415 | 139.2007 | 153.1274 | 152.3294 | 1025.6677 | 1312.9487 | 1106.0878 | 745.1925 | 14.1271
2025-01-05 | 45660 | 514.6451 | 0.68517 | 121.5042 | 12.6065 | 100.441 | 17.9045 | 35.3724 | 24.562 | 1826.3271 | 6.5147 | 3.9018 | 126.0728 | 124.4142 | 106.9103 | 133.7286 | 147.4517 | 146.6191 | 1001.9395 | 1237.5105 | 1071.0045 | 755.3611 | 11.7513
2025-01-06 | 45660.0417 | 552.5621 | 0.65432 | 112.8472 | 7.6968 | 95.4367 | 11.6249 | 30.9571 | 16.8692 | 1922.6407 | 7.072 | 4.1676 | 128.3307 | 126.5914 | 108.4529 | 136.3955 | 150.7049 | 149.7967 | 1101.4419 | 1370.8467 | 1160.1307 | 762.5516 | 14.8106
2025-01-06 | 45660.0833 | 496.8051 | 0.66611 | 97.0238 | 13.5086 | 66.8926 | 17.3549 | 22.7162 | 16.2875 | 1694.6844 | 6.305 | 3.9692 | 125.8264 | 125.0888 | 107.4707 | 134.1706 | 147.3021 | 146.8283 | 917.2173 | 1122.3329 | 999.7322 | 694.997 | 7.9073
2025-01-06 | 45660.125 | 562.2791 | 0.67713 | 131.0443 | 12.4803 | 115.5646 | 16.6064 | 37.9648 | 26.7841 | 1886.5442 | 4.0446 | 3.5733 | 130.5573 | 128.5888 | 110.5878 | 136.0292 | 150.059 | 149.2828 | 1095.7416 | 1322.6615 | 1092.6855 | 793.8366 | 7.4841
2025-01-06 | 45660.1667 | 458.3483 | 0.65379 | 93.9122 | 10.6697 | 74.6661 | 12.6172 | 22.1667 | 13.5554 | 1584.3514 | 7.1275 | 4.4742 | 125.9157 | 125.6323 | 108.4068 | 134.748 | 147.969 | 147.7205 | 830.5578 | 1031.8441 | 889.9312 | 694.4199 | 11.0451
2025-01-06 | 45660.2083 | 342.463 | 0.6793 | 81.6189 | 6.3032 | 72.4978 | 11.2665 | 12.7652 | 5.9822 | 1366.4548 | 9.6481 | 5.4298 | 116.7638 | 117.668 | 102.8246 | 125.298 | 137.5306 | 137.3624 | 632.1323 | 775.1387 | 794.7798 | 571.6948 | 8.0588
2025-01-06 | 45660.25 | 398.9447 | 0.72928 | 93.5945 | 9.7333 | 81.6435 | 19.8134 | 23.7582 | 17.8095 | 1557.2334 | 8.2074 | 4.536 | 120.399 | 119.3294 | 104.3759 | 122.4342 | 135.1018 | 134.5455 | 778.8044 | 898.4446 | 854.9489 | 702.2862 | 4.8455
2025-01-06 | 45660.2917 | 546.4293 | 0.70205 | 128.3652 | 12.0864 | 109.1451 | 18.3908 | 33.6353 | 24.9152 | 1921.4747 | 5.6219 | 4.217 | 129.9584 | 128.1492 | 109.9622 | 132.697 | 147.0137 | 146.2198 | 1121.3042 | 1323.4359 | 1112.9258 | 808.5371 | 9.5724
2025-01-06 | 45660.3333 | 583.019 | 0.68582 | 139.3282 | 19.0535 | 110.5998 | 23.1386 | 37.8152 | 30.8698 | 1936.405 | 2.7947 | 3.7305 | 131.3787 | 129.6942 | 110.7646 | 137.2099 | 151.7703 | 151.2755 | 1141.0081 | 1384.0922 | 1129.0479 | 807.3906 | 9.4763
2025-01-06 | 45660.375 | 585.3808 | 0.68299 | 143.3283 | 12.7289 | 117.195 | 10.2737 | 40.784 | 33.3552 | 1959.6642 | 1.8475 | 3.7027 | 130.7818 | 128.7176 | 109.9717 | 138.1132 | 152.9887 | 152.3087 | 1156.7344 | 1429.8579 | 1159.7292 | 799.9235 | 10.8501
2025-01-06 | 45660.4167 | 588.1453 | 0.67912 | 145.3739 | 9.9983 | 117.8944 | 8.3126 | 39.4219 | 29.7437 | 1990.3882 | 2.8637 | 4.0055 | 131.309 | 129.0886 | 110.413 | 139.6756 | 154.5105 | 153.687 | 1180.8839 | 1486.9038 | 1200.4049 | 789.9506 | 16.2769
2025-01-06 | 45660.4583 | 592.0438 | 0.67416 | 131.7925 | 15.0067 | 102.7258 | 11.5919 | 32.501 | 32.04 | 2007.0773 | 1.9579 | 4.1298 | 130.2566 | 127.9493 | 109.596 | 141.8295 | 156.5758 | 155.6265 | 1176.8154 | 1528.2782 | 1224.4661 | 782.6023 | 19.245
2025-01-06 | 45660.5 | 588.3351 | 0.67093 | 130.0762 | 12.8198 | 104.5244 | 4.2539 | 34.559 | 33.0648 | 2015.0167 | 3.0246 | 4.1569 | 130.7418 | 128.46 | 110.2754 | 143.2436 | 157.7623 | 156.6544 | 1169.2758 | 1540.4386 | 1231.6423 | 783.3802 | 23.1749
2025-01-06 | 45660.5417 | 576.65 | 0.67217 | 119.825 | 11.9813 | 98.0774 | 11.3503 | 36.2447 | 26.85 | 1993.1764 | 4.3679 | 4.2274 | 130.5559 | 128.3505 | 110.4937 | 145.4952 | 159.5772 | 158.6307 | 1134.4625 | 1531.7574 | 1210.2883 | 782.8823 | 24.3678
2025-01-06 | 45660.5833 | 565.3521 | 0.6756 | 102.2689 | 9.2669 | 74.3468 | 10.3601 | 30.5507 | 26.6607 | 1967.1514 | 4.5789 | 4.1352 | 129.8817 | 127.9925 | 110.1763 | 144.3832 | 158.7418 | 157.9267 | 1100.6616 | 1476.444 | 1192.2717 | 774.8955 | 19.3084
2025-01-06 | 45660.625 | 471.631 | 0.67567 | 93.1887 | 13.5871 | 66.4871 | 10.5964 | 16.3527 | 14.0748 | 1676.6165 | 6.167 | 4.2874 | 125.359 | 124.7169 | 108.4227 | 140.9764 | 153.5328 | 152.9003 | 853.1666 | 1127.8357 | 973.554 | 703.0788 | 16.7858
2025-01-06 | 45660.6667 | 563.7596 | 0.69088 | 136.9494 | 11.9663 | 107.9531 | 12.4088 | 23.9988 | 21.1605 | 1925.2648 | 3.9575 | 3.6164 | 133.6307 | 131.3062 | 113.8313 | 140.5283 | 153.897 | 152.9754 | 1109.4703 | 1367.3109 | 1129.4003 | 795.8652 | 12.8971
2025-01-06 | 45660.7083 | 578.9482 | 0.68652 | 131.0763 | 13.6712 | 107.9927 | 15.6212 | 31.8383 | 28.1547 | 1924.5088 | 2.3078 | 3.542 | 134.5175 | 132.4836 | 114.5628 | 144.1297 | 157.6304 | 156.9867 | 1113.1454 | 1405.4645 | 1133.9351 | 790.5935 | 14.3354
2025-01-06 | 45660.75 | 587.2761 | 0.68394 | 132.4111 | 13.0764 | 111.1458 | 14.6512 | 31.8609 | 31.8749 | 1951.0885 | 1.0524 | 3.5048 | 135.6663 | 133.4196 | 115.4081 | 144.101 | 157.6436 | 157.1788 | 1137.8643 | 1430.3409 | 1163.3281 | 787.7615 | 11.6866
2025-01-06 | 45660.7917 | 592.0993 | 0.67052 | 126.085 | 9.3683 | 111.7664 | 16.4669 | 36.6451 | 33.3327 | 1958.368 | 1.3824 | 3.6636 | 134.2594 | 131.8919 | 113.8022 | 143.2923 | 157.2015 | 156.5689 | 1139.5892 | 1450.895 | 1167.3081 | 791.0427 | 12.5521
2025-01-06 | 45660.8333 | 590.3998 | 0.65707 | 104.6222 | 7.3377 | 88.7775 | 8.1663 | 35.6734 | 32.7622 | 1940.8182 | 1.1842 | 3.6643 | 132.8867 | 130.7247 | 112.5214 | 141.5474 | 155.6486 | 155.0228 | 1123.1926 | 1422.5878 | 1152.6689 | 788.1221 | 9.2533
2025-01-06 | 45660.875 | 592.297 | 0.64901 | 103.969 | 8.0293 | 111.1733 | 16.9768 | 41.979 | 30.3236 | 1950.5007 | 1.8761 | 3.4042 | 132.8907 | 130.7559 | 112.4362 | 139.7909 | 154.0123 | 153.2072 | 1138.134 | 1414.2635 | 1163.9268 | 786.6033 | 9.0474
2025-01-06 | 45660.9167 | 588.6329 | 0.64759 | 111.873 | 7.6608 | 113.0977 | 17.8847 | 46.0802 | 29.9029 | 1936.4451 | 1.9155 | 3.3547 | 130.8008 | 128.43 | 110.2858 | 138.7249 | 152.8443 | 151.8309 | 1117.2179 | 1393.4269 | 1147.0198 | 789.4217 | 9.4035
2025-01-06 | 45660.9583 | 589.4096 | 0.64921 | 125.5217 | 9.3758 | 105.6119 | 15.01 | 45.1759 | 33.4685 | 1942.3799 | 1.0969 | 3.063 | 129.8192 | 127.4064 | 109.0805 | 137.604 | 151.8197 | 150.767 | 1125.1801 | 1401.6827 | 1153.4304 | 788.9765 | 8.2417
2025-01-06 | 45661 | 571.0611 | 0.63061 | 119.9072 | 10.3407 | 110.0656 | 10.2726 | 42.7781 | 37.0232 | 1932.6737 | 4.0167 | 2.4631 | 128.6367 | 126.3391 | 108.0754 | 137.3691 | 151.6503 | 150.4822 | 1112.5685 | 1391.1791 | 1140.8464 | 791.8624 | 13.0455
Note:- | 19:00 to 00:00 Hrs data of 18/12/2024 are not consider due to Boiler Shutdown because of BTL.
17:00 to 21:00 Hrs data of 24/12/2024 are not considered due to Unit tripping because of low drum level.